## Datos x2,5
Mayoración x2,5. Las potencias de las líneas, están mayoradas 2,5 respecto a las potencias que aparecen en la hoja P-H |  |  | Distribución de potencias en función de la potencia contratada | [8 empty] | esta hoja es la que se ha utilizado para realizar las simulaciones, ver en el libro resumen
línea Empalme-Corral del Acabose.
Alias | P. Contratada (kW) | % del total de P.contratada | Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
|  |  | (MW y Mvar) | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q
CRAL.ACABOSE_1 | 1192.7 | 20.88% | CRAL.ACABOSE_1 | 0.45383 | 0.24777 | 0.36497 | 0.19925 | 0.31419 | 0.17153 | 0.28087 | 0.15334 | 0.26341 | 0.14381 | 0.24437 | 0.13341 | 0.23644 | 0.12908 | 0.24754 | 0.13515 | 0.28721 | 0.1568 | 0.33482 | 0.18279 | 0.37449 | 0.20445 | 0.43796 | 0.2391 | 0.49191 | 0.26856 | 0.6141 | 0.33526 | 0.74105 | 0.40457 | 0.81563 | 0.44529 | 0.73787 | 0.40284 | 0.7109 | 0.38811 | 0.68868 | 0.37598 | 0.59188 | 0.32314 | 0.52524 | 0.28675 | 0.53793 | 0.29368 | 0.5776 | 0.31534 | 0.53476 | 0.29195
CRAL.ACABOSE_2 | 1326 | 23.21% | CRAL.ACABOSE_2 | 0.50455 | 0.27546 | 0.40576 | 0.22152 | 0.34931 | 0.1907 | 0.31226 | 0.17048 | 0.29285 | 0.15988 | 0.27168 | 0.14832 | 0.26286 | 0.14351 | 0.27521 | 0.15025 | 0.31931 | 0.17433 | 0.37224 | 0.20322 | 0.41634 | 0.2273 | 0.48691 | 0.26583 | 0.54689 | 0.29857 | 0.68273 | 0.37273 | 0.82387 | 0.44979 | 0.90678 | 0.49505 | 0.82034 | 0.44786 | 0.79035 | 0.43149 | 0.76565 | 0.418 | 0.65804 | 0.35925 | 0.58394 | 0.3188 | 0.59805 | 0.3265 | 0.64216 | 0.35058 | 0.59453 | 0.32458
E.SIRIO_4 | 3194.6 | 55.92% | E.SIRIO_4 | 1.2156 | 0.66363 | 0.97756 | 0.53369 | 0.84155 | 0.45944 | 0.75229 | 0.41071 | 0.70554 | 0.38519 | 0.65454 | 0.35734 | 0.63329 | 0.34574 | 0.66304 | 0.36198 | 0.76929 | 0.41999 | 0.8968 | 0.4896 | 1.0031 | 0.54761 | 1.1731 | 0.64043 | 1.3176 | 0.71932 | 1.6448 | 0.89799 | 1.9849 | 1.0836 | 2.1846 | 1.1927 | 1.9764 | 1.079 | 1.9041 | 1.0395 | 1.8446 | 1.0071 | 1.5853 | 0.86551 | 1.4068 | 0.76805 | 1.4408 | 0.78661 | 1.5471 | 0.84462 | 1.4323 | 0.78197
Total potencia contratada(kW) | 5713.3 | 100% | Total | 2.174 | 1.1869 | 1.7483 | 0.95447 | 1.505 | 0.82167 | 1.3454 | 0.73452 | 1.2618 | 0.68888 | 1.1706 | 0.63908 | 1.1326 | 0.61833 | 1.1858 | 0.64738 | 1.3758 | 0.75112 | 1.6039 | 0.87562 | 1.7939 | 0.97937 | 2.0979 | 1.1454 | 2.3564 | 1.2865 | 2.9417 | 1.606 | 3.5498 | 1.938 | 3.907 | 2.133 | 3.5346 | 1.9297 | 3.4054 | 1.8591 | 3.2989 | 1.801 | 2.8353 | 1.5479 | 2.516 | 1.3736 | 2.5768 | 1.4068 | 2.7668 | 1.5105 | 2.5616 | 1.3985
Línea Empalme-Estrella Sirio.
Alias | P. Contratada (kW) | % del total de P.contratada | Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
|  |  | (MW y Mvar) | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q
E.SIRIO_1 | 672.7 | 0.097735 | E.SIRIO_1 | 0.26935 | 0.14606 | 0.22693 | 0.12306 | 0.20313 | 0.11015 | 0.18824 | 0.10208 | 0.17932 | 0.09724 | 0.16741 | 0.090784 | 0.15402 | 0.083521 | 0.13542 | 0.073434 | 0.14509 | 0.07868 | 0.15848 | 0.085942 | 0.18973 | 0.10289 | 0.19568 | 0.10612 | 0.22693 | 0.12306 | 0.28869 | 0.15655 | 0.3564 | 0.19327 | 0.37872 | 0.20537 | 0.36086 | 0.19569 | 0.34821 | 0.18883 | 0.32217 | 0.17471 | 0.30134 | 0.16341 | 0.25818 | 0.14001 | 0.28423 | 0.15413 | 0.31994 | 0.1735 | 0.29688 | 0.16099
E.SIRIO_2 | 2202.9 | 0.32005 | E.SIRIO_2 | 0.88203 | 0.47831 | 0.74315 | 0.403 | 0.66518 | 0.36071 | 0.61645 | 0.33429 | 0.58721 | 0.31843 | 0.54822 | 0.29729 | 0.50437 | 0.27351 | 0.44345 | 0.24048 | 0.47513 | 0.25765 | 0.51898 | 0.28144 | 0.62132 | 0.33693 | 0.64081 | 0.3475 | 0.74315 | 0.403 | 0.94538 | 0.51266 | 1.1671 | 0.6329 | 1.2402 | 0.67254 | 1.1817 | 0.64083 | 1.1403 | 0.61837 | 1.055 | 0.57212 | 0.9868 | 0.53513 | 0.84548 | 0.45849 | 0.93076 | 0.50474 | 1.0477 | 0.56816 | 0.97218 | 0.5272
E.SIRIO_3 | 1681.5 | 0.2443 | E.SIRIO_3 | 0.67326 | 0.3651 | 0.56725 | 0.30761 | 0.50774 | 0.27534 | 0.47054 | 0.25517 | 0.44822 | 0.24306 | 0.41847 | 0.22693 | 0.38499 | 0.20877 | 0.33849 | 0.18356 | 0.36267 | 0.19667 | 0.39615 | 0.21482 | 0.47426 | 0.25718 | 0.48914 | 0.26525 | 0.56725 | 0.30761 | 0.72162 | 0.39132 | 0.89087 | 0.4831 | 0.94666 | 0.51336 | 0.90203 | 0.48915 | 0.87041 | 0.47201 | 0.80531 | 0.43671 | 0.75324 | 0.40847 | 0.64537 | 0.34997 | 0.71046 | 0.38527 | 0.79973 | 0.43368 | 0.74208 | 0.40242
I.E.S.J.VERNE | 206.4 | 0.029987 | I.E.S.J.VERNE | 0.082642 | 0.044815 | 0.069629 | 0.037759 | 0.062324 | 0.033797 | 0.057758 | 0.031321 | 0.055018 | 0.029835 | 0.051366 | 0.027855 | 0.047256 | 0.025626 | 0.041549 | 0.022531 | 0.044517 | 0.024141 | 0.048626 | 0.026369 | 0.058214 | 0.031569 | 0.060041 | 0.032559 | 0.069629 | 0.037759 | 0.088577 | 0.048034 | 0.10935 | 0.0593 | 0.1162 | 0.063014 | 0.11072 | 0.060042 | 0.10684 | 0.057938 | 0.09885 | 0.053605 | 0.092458 | 0.050138 | 0.079217 | 0.042958 | 0.087207 | 0.047291 | 0.098165 | 0.053233 | 0.091088 | 0.049396
ESTRELLA.ALTAIR | 1077.5 | 0.15655 | ESTRELLA.ALTAIR | 0.43143 | 0.23395 | 0.36349 | 0.19712 | 0.32536 | 0.17644 | 0.30152 | 0.16351 | 0.28722 | 0.15575 | 0.26815 | 0.14541 | 0.2467 | 0.13378 | 0.2169 | 0.11762 | 0.2324 | 0.12603 | 0.25385 | 0.13766 | 0.3039 | 0.1648 | 0.31344 | 0.16997 | 0.36349 | 0.19712 | 0.46241 | 0.25076 | 0.57086 | 0.30957 | 0.60662 | 0.32896 | 0.57801 | 0.31345 | 0.55775 | 0.30246 | 0.51604 | 0.27984 | 0.48267 | 0.26175 | 0.41355 | 0.22426 | 0.45526 | 0.24688 | 0.51247 | 0.2779 | 0.47552 | 0.25787
AGRICULTORES | 1041.9 | 0.15138 | AGRICULTORES | 0.41717 | 0.22623 | 0.35148 | 0.1906 | 0.31461 | 0.17061 | 0.29156 | 0.15811 | 0.27773 | 0.15061 | 0.25929 | 0.14061 | 0.23855 | 0.12936 | 0.20974 | 0.11374 | 0.22472 | 0.12186 | 0.24546 | 0.13311 | 0.29386 | 0.15936 | 0.30308 | 0.16436 | 0.35148 | 0.1906 | 0.44713 | 0.24247 | 0.552 | 0.29934 | 0.58658 | 0.31809 | 0.55892 | 0.30309 | 0.53933 | 0.29247 | 0.49899 | 0.2706 | 0.46673 | 0.2531 | 0.39989 | 0.21685 | 0.44022 | 0.23872 | 0.49554 | 0.26872 | 0.45981 | 0.24935
AGRICULTORES_2 | 0 | 0 | AGRICULTORES_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E.SIRIO | 0 | 0 | E.SIRIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total potencia contratada (kW) | 6882.9 |  | Total | 2.7559 | 1.4945 | 2.3219 | 1.2592 | 2.0783 | 1.127 | 1.9261 | 1.0445 | 1.8347 | 0.99494 | 1.7129 | 0.92888 | 1.5759 | 0.85457 | 1.3856 | 0.75136 | 1.4845 | 0.80503 | 1.6216 | 0.87934 | 1.9413 | 1.0527 | 2.0022 | 1.0858 | 2.3219 | 1.2592 | 2.9538 | 1.6018 | 3.6466 | 1.9775 | 3.875 | 2.1013 | 3.6923 | 2.0023 | 3.5628 | 1.9321 | 3.2964 | 1.7876 | 3.0832 | 1.672 | 2.6417 | 1.4325 | 2.9081 | 1.577 | 3.2736 | 1.7752 | 3.0376 | 1.6472
|  |  |  | 4.9298 | 2.6813 | 4.0702 | 2.2136 | 3.5834 | 1.9487 | 3.2715 | 1.779 | 3.0965 | 1.6838 | 2.8835 | 1.568 | 2.7085 | 1.4729 | 2.5713 | 1.3987 | 2.8603 | 1.5562 | 3.2254 | 1.755 | 3.7352 | 2.0321 | 4.1001 | 2.2311 | 4.6783 | 2.5456 | 5.8955 | 3.2078 | 7.1964 | 3.9155 | 7.782 | 4.2344 | 7.2268 | 3.9319 | 6.9682 | 3.7912 | 6.5953 | 3.5886 | 5.9185 | 3.2199 | 5.1577 | 2.8061 | 5.485 | 2.9838 | 6.0404 | 3.2857 | 5.5992 | 3.0457
Transformador de Potencia |  |  |  | 2.7559 |  | 2.3219 |  | 2.0783 |  | 1.9261 |  | 1.8347 |  | 1.7129 |  | 1.5759 |  | 1.3856 |  | 1.4845 |  | 1.6216 |  | 1.9413 |  | 2.0022 |  | 2.3219 |  | 2.9538 |  | 3.6466 |  | 3.875 |  | 3.6923 |  | 3.5628 |  | 3.2964 |  | 3.0832 |  | 2.6417 |  | 2.9081 |  | 3.2736 |  | 3.0376
Sn (MVA) | 3.55 | [34 empty] | 5% |  |  |  |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
Ucc | 10% | [39 empty] | P | Q | P | Q | P | Q | P | Q | P | Q
Scc(MVA) | 35 | [39 empty] | 0.33223 | 0.18016 | 0.28465 | 0.15436 | 0.31336 | 0.16993 | 0.35273 | 0.19128 | 0.32731 | 0.17749
[41 empty] | 1.0879 | 0.58998 | 0.93214 | 0.50549 | 1.0262 | 0.55647 | 1.1551 | 0.62639 | 1.0718 | 0.58124
[41 empty] | 0.83044 | 0.45034 | 0.71152 | 0.38584 | 0.78328 | 0.42476 | 0.88171 | 0.47813 | 0.81814 | 0.44366
[41 empty] | 0.10194 | 0.055278 | 0.087337 | 0.047361 | 0.096146 | 0.052138 | 0.10823 | 0.05869 | 0.10042 | 0.054459
[41 empty] | 0.53215 | 0.28857 | 0.45594 | 0.24725 | 0.50193 | 0.27219 | 0.56499 | 0.30639 | 0.52426 | 0.2843
[41 empty] | 0.51456 | 0.27904 | 0.44087 | 0.23908 | 0.48534 | 0.26319 | 0.54633 | 0.29626 | 0.50694 | 0.27491
[41 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | hora más favorable | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | hora más desfavorable | [35 empty] | 0.34884 | 0.18917 | 0.29888 | 0.16208 | 0.32903 | 0.17843 | 0.37037 | 0.20085 | 0.34367 | 0.18637
[41 empty] | 1.1423 | 0.61948 | 0.97875 | 0.53076 | 1.0775 | 0.5843 | 1.2129 | 0.65771 | 1.1254 | 0.6103
[41 empty] | 0.87197 | 0.47285 | 0.74709 | 0.40514 | 0.82245 | 0.446 | 0.92579 | 0.50204 | 0.85905 | 0.46585
[41 empty] | 0.10703 | 0.058042 | 0.091704 | 0.049729 | 0.10095 | 0.054745 | 0.11364 | 0.061624 | 0.10545 | 0.057182
[41 empty] | 0.55875 | 0.303 | 0.47873 | 0.25961 | 0.52702 | 0.2858 | 0.59324 | 0.32171 | 0.55048 | 0.29851
[41 empty] | 0.54029 | 0.29299 | 0.46292 | 0.25103 | 0.50961 | 0.27635 | 0.57364 | 0.31108 | 0.53229 | 0.28865
[41 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[41 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[17 empty] | 3.3993 | 1.8434 | 2.9125 | 1.5794 | 3.2062 | 1.7387 | 3.6091 | 1.9572 | 3.3489 | 1.8161
[17 empty] | 3.3993 | 1.8434 | 2.9125 | 1.5794 | 3.2062 | 1.7387 | 3.6091 | 1.9572 | 3.3489 | 1.8161

## DEMANDA 5 % ANUAL
SE SUPONE UN CRECIMIENTO ANUAL DEL 5% RESPECTO AL AÑO ANTERIOR ( NO RESPECTO AL AÑO BASE) | [13 empty] | 5%
OJO EL AÑO 0 ES EL QUE APARECE EN LA HOJA DATOS X 2,5
LINEA EMPALME-CORRAL DEL ACABOSE AÑO 1
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
| P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar)
CRAL.ACABOSE_1 | 0.47652 | 0.26016 | 0.38322 | 0.20922 | 0.3299 | 0.18011 | 0.29491 | 0.16101 | 0.27658 | 0.151 | 0.25659 | 0.14008 | 0.24826 | 0.13554 | 0.25992 | 0.1419 | 0.30158 | 0.16464 | 0.35156 | 0.19193 | 0.39321 | 0.21467 | 0.45986 | 0.25106 | 0.51651 | 0.28199 | 0.64481 | 0.35203 | 0.7781 | 0.4248 | 0.85641 | 0.46755 | 0.77477 | 0.42298 | 0.74644 | 0.40752 | 0.72311 | 0.39478 | 0.62148 | 0.33929 | 0.5515 | 0.30109 | 0.56483 | 0.30837 | 0.60648 | 0.33111 | 0.5615 | 0.30655
CRAL.ACABOSE_2 | 0.52978 | 0.28923 | 0.42605 | 0.2326 | 0.36677 | 0.20024 | 0.32787 | 0.179 | 0.30749 | 0.16788 | 0.28527 | 0.15574 | 0.276 | 0.15068 | 0.28897 | 0.15776 | 0.33528 | 0.18304 | 0.39085 | 0.21338 | 0.43716 | 0.23867 | 0.51126 | 0.27912 | 0.57424 | 0.3135 | 0.71687 | 0.39137 | 0.86506 | 0.47228 | 0.95212 | 0.51981 | 0.86136 | 0.47025 | 0.82987 | 0.45306 | 0.80393 | 0.4389 | 0.69094 | 0.37721 | 0.61314 | 0.33474 | 0.62796 | 0.34283 | 0.67427 | 0.36811 | 0.62425 | 0.34081
E.SIRIO_4 | 1.2763 | 0.69681 | 1.0264 | 0.56038 | 0.88362 | 0.48241 | 0.78991 | 0.43125 | 0.74082 | 0.40445 | 0.68726 | 0.37521 | 0.66495 | 0.36303 | 0.69619 | 0.38008 | 0.80776 | 0.44099 | 0.94164 | 0.51408 | 1.0532 | 0.57499 | 1.2317 | 0.67245 | 1.3835 | 0.75529 | 1.7271 | 0.94289 | 2.0841 | 1.1378 | 2.2939 | 1.2523 | 2.0752 | 1.1329 | 1.9993 | 1.0915 | 1.9368 | 1.0574 | 1.6646 | 0.90878 | 1.4772 | 0.80645 | 1.5129 | 0.82595 | 1.6244 | 0.88686 | 1.5039 | 0.82107
TOTAL | 2.2826 | 1.2462 | 1.8357 | 1.0022 | 1.5803 | 0.86275 | 1.4127 | 0.77125 | 1.3249 | 0.72332 | 1.2291 | 0.67103 | 1.1892 | 0.64924 | 1.2451 | 0.67975 | 1.4446 | 0.78868 | 1.6841 | 0.9194 | 1.8836 | 1.0283 | 2.2028 | 1.2026 | 2.4742 | 1.3508 | 3.0888 | 1.6863 | 3.7273 | 2.0349 | 4.1024 | 2.2397 | 3.7113 | 2.0262 | 3.5756 | 1.9521 | 3.4639 | 1.8911 | 2.977 | 1.6253 | 2.6418 | 1.4423 | 2.7057 | 1.4771 | 2.9052 | 1.5861 | 2.6897 | 1.4684
LINEA EMPALME-CORRAL DEL ACABOSE AÑO 2
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
| P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar)
CRAL.ACABOSE_1 | 0.50035 | 0.27316 | 0.40238 | 0.21968 | 0.3464 | 0.18911 | 0.30966 | 0.16906 | 0.29041 | 0.15855 | 0.26942 | 0.14709 | 0.26067 | 0.14231 | 0.27292 | 0.149 | 0.31665 | 0.17288 | 0.36914 | 0.20153 | 0.41288 | 0.22541 | 0.48285 | 0.26361 | 0.54234 | 0.29609 | 0.67705 | 0.36963 | 0.817 | 0.44604 | 0.89923 | 0.49093 | 0.8135 | 0.44413 | 0.78376 | 0.42789 | 0.75927 | 0.41452 | 0.65255 | 0.35626 | 0.57907 | 0.31614 | 0.59307 | 0.32378 | 0.63681 | 0.34766 | 0.58957 | 0.32187
CRAL.ACABOSE_2 | 0.55627 | 0.30369 | 0.44735 | 0.24423 | 0.38511 | 0.21025 | 0.34426 | 0.18795 | 0.32287 | 0.17627 | 0.29953 | 0.16353 | 0.2898 | 0.15822 | 0.30342 | 0.16565 | 0.35204 | 0.1922 | 0.41039 | 0.22405 | 0.45902 | 0.2506 | 0.53682 | 0.29307 | 0.60295 | 0.32918 | 0.75271 | 0.41094 | 0.90831 | 0.49589 | 0.99973 | 0.5458 | 0.90442 | 0.49377 | 0.87136 | 0.47571 | 0.84413 | 0.46085 | 0.72548 | 0.39607 | 0.64379 | 0.35148 | 0.65935 | 0.35997 | 0.70798 | 0.38652 | 0.65546 | 0.35785
E.SIRIO_4 | 1.3402 | 0.73166 | 1.0778 | 0.58839 | 0.92781 | 0.50653 | 0.8294 | 0.45281 | 0.77786 | 0.42467 | 0.72163 | 0.39397 | 0.6982 | 0.38118 | 0.731 | 0.39908 | 0.84815 | 0.46304 | 0.98872 | 0.53979 | 1.1059 | 0.60374 | 1.2933 | 0.70607 | 1.4526 | 0.79305 | 1.8134 | 0.99004 | 2.1883 | 1.1947 | 2.4085 | 1.3149 | 2.1789 | 1.1896 | 2.0993 | 1.1461 | 2.0337 | 1.1103 | 1.7478 | 0.95422 | 1.551 | 0.84678 | 1.5885 | 0.86724 | 1.7057 | 0.9312 | 1.5791 | 0.86213
TOTAL | 2.3968 | 1.3085 | 1.9275 | 1.0523 | 1.6593 | 0.90589 | 1.4833 | 0.80981 | 1.3911 | 0.75949 | 1.2906 | 0.70458 | 1.2487 | 0.68171 | 1.3073 | 0.71373 | 1.5168 | 0.82811 | 1.7683 | 0.96537 | 1.9778 | 1.0798 | 2.313 | 1.2628 | 2.5979 | 1.4183 | 3.2432 | 1.7706 | 3.9136 | 2.1366 | 4.3075 | 2.3517 | 3.8969 | 2.1275 | 3.7544 | 2.0497 | 3.6371 | 1.9856 | 3.1259 | 1.7066 | 2.7739 | 1.5144 | 2.8409 | 1.551 | 3.0505 | 1.6654 | 2.8242 | 1.5418
| 2.3968 |  | 1.9275 |  | 1.6593 |  | 1.4833 |  | 1.3911 |  | 1.2906 |  | 1.2487 |  | 1.3073 |  | 1.5168 |  | 1.7683 |  | 1.9778 |  | 2.313 |  | 2.5979 |  | 3.2432 |  | 3.9136 |  | 4.3075 |  | 3.8969 |  | 3.7544 |  | 3.6371 |  | 3.1259 |  | 2.7739 |  | 2.8409 |  | 3.0505 |  | 2.8242
LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
| P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar) | P (MW) | Q(Mvar)
CRAL.ACABOSE_1 | 0.52537 | 0.28682 | 0.4225 | 0.23066 | 0.36372 | 0.19857 | 0.32514 | 0.17751 | 0.30493 | 0.16648 | 0.28289 | 0.15444 | 0.2737 | 0.14943 | 0.28656 | 0.15645 | 0.33249 | 0.18152 | 0.3876 | 0.21161 | 0.43352 | 0.23668 | 0.507 | 0.27679 | 0.56945 | 0.31089 | 0.7109 | 0.38811 | 0.85785 | 0.46834 | 0.94419 | 0.51548 | 0.85418 | 0.46633 | 0.82295 | 0.44929 | 0.79723 | 0.43525 | 0.68518 | 0.37407 | 0.60803 | 0.33195 | 0.62272 | 0.33997 | 0.66865 | 0.36504 | 0.61905 | 0.33797
CRAL.ACABOSE_2 | 0.58408 | 0.31888 | 0.46972 | 0.25644 | 0.40436 | 0.22076 | 0.36148 | 0.19735 | 0.33901 | 0.18508 | 0.31451 | 0.1717 | 0.30429 | 0.16613 | 0.31859 | 0.17393 | 0.36965 | 0.20181 | 0.43091 | 0.23526 | 0.48197 | 0.26313 | 0.56366 | 0.30773 | 0.6331 | 0.34564 | 0.79035 | 0.43149 | 0.95373 | 0.52068 | 1.0497 | 0.57309 | 0.94965 | 0.51845 | 0.91493 | 0.4995 | 0.88634 | 0.48389 | 0.76176 | 0.41588 | 0.67598 | 0.36905 | 0.69232 | 0.37797 | 0.74338 | 0.40584 | 0.68824 | 0.37574
E.SIRIO_4 | 1.4072 | 0.76824 | 1.1316 | 0.61781 | 0.9742 | 0.53186 | 0.87087 | 0.47545 | 0.81675 | 0.4459 | 0.75771 | 0.41367 | 0.73311 | 0.40024 | 0.76755 | 0.41904 | 0.89055 | 0.48619 | 1.0382 | 0.56678 | 1.1612 | 0.63393 | 1.358 | 0.74138 | 1.5253 | 0.83271 | 1.9041 | 1.0395 | 2.2977 | 1.2544 | 2.529 | 1.3807 | 2.2879 | 1.2491 | 2.2042 | 1.2034 | 2.1354 | 1.1658 | 1.8352 | 1.0019 | 1.6286 | 0.88912 | 1.6679 | 0.9106 | 1.7909 | 0.97776 | 1.6581 | 0.90523
TOTAL | 2.5166 | 1.3739 | 2.0239 | 1.1049 | 1.7423 | 0.95119 | 1.5575 | 0.8503 | 1.4607 | 0.79746 | 1.3551 | 0.73981 | 1.3111 | 0.71579 | 1.3727 | 0.74942 | 1.5927 | 0.86952 | 1.8567 | 1.0136 | 2.0767 | 1.1337 | 2.4286 | 1.3259 | 2.7278 | 1.4892 | 3.4054 | 1.8591 | 4.1093 | 2.2435 | 4.5229 | 2.4692 | 4.0917 | 2.2338 | 3.9421 | 2.1522 | 3.8189 | 2.0849 | 3.2822 | 1.7919 | 2.9126 | 1.5901 | 2.983 | 1.6285 | 3.203 | 1.7486 | 2.9654 | 1.6189
| 2.5166 |  | 2.0239 |  | 1.7423 |  | 1.5575 |  | 1.4607 |  | 1.3551 |  | 1.3111 |  | 1.3727 |  | 1.5927 |  | 1.8567 |  | 2.0767 |  | 2.4286 |  | 2.7278 |  | 3.4054 |  | 4.1093 |  | 4.5229 |  | 4.0917 |  | 3.9421 |  | 3.8189 |  | 3.2822 |  | 2.9126 |  | 2.983 |  | 3.203 |  | 2.9654
LINEA EMPALME ESTRELLA SIRIO. AÑO 1
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
(MW y Mvar) | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q
E.SIRIO_1 | 0.28281 | 0.15336 | 0.23828 | 0.12922 | 0.21328 | 0.11566 | 0.19766 | 0.10719 | 0.18828 | 0.1021 | 0.17578 | 0.095323 | 0.16172 | 0.087698 | 0.14219 | 0.077106 | 0.15234 | 0.082614 | 0.16641 | 0.09024 | 0.19922 | 0.10803 | 0.20547 | 0.11142 | 0.23828 | 0.12922 | 0.30313 | 0.16438 | 0.37422 | 0.20293 | 0.39766 | 0.21564 | 0.37891 | 0.20547 | 0.36563 | 0.19827 | 0.33828 | 0.18344 | 0.31641 | 0.17158 | 0.27109 | 0.14701 | 0.29844 | 0.16184 | 0.33594 | 0.18217 | 0.31172 | 0.16904
E.SIRIO_2 | 0.92613 | 0.50223 | 0.7803 | 0.42315 | 0.69844 | 0.37875 | 0.64727 | 0.351 | 0.61657 | 0.33435 | 0.57563 | 0.31216 | 0.52958 | 0.28718 | 0.46562 | 0.2525 | 0.49888 | 0.27054 | 0.54493 | 0.29551 | 0.65239 | 0.35378 | 0.67285 | 0.36488 | 0.7803 | 0.42315 | 0.99265 | 0.5383 | 1.2255 | 0.66455 | 1.3022 | 0.70617 | 1.2408 | 0.67287 | 1.1973 | 0.64929 | 1.1078 | 0.60073 | 1.0361 | 0.56188 | 0.88776 | 0.48142 | 0.9773 | 0.52997 | 1.1001 | 0.59657 | 1.0208 | 0.55356
E.SIRIO_3 | 0.70693 | 0.38336 | 0.59562 | 0.32299 | 0.53312 | 0.2891 | 0.49407 | 0.26792 | 0.47063 | 0.25522 | 0.43939 | 0.23827 | 0.40424 | 0.21921 | 0.35542 | 0.19274 | 0.3808 | 0.2065 | 0.41595 | 0.22557 | 0.49797 | 0.27004 | 0.5136 | 0.27851 | 0.59562 | 0.32299 | 0.7577 | 0.41089 | 0.93541 | 0.50726 | 0.99399 | 0.53903 | 0.94713 | 0.51361 | 0.91393 | 0.49561 | 0.84558 | 0.45854 | 0.7909 | 0.42889 | 0.67763 | 0.36747 | 0.74598 | 0.40453 | 0.83972 | 0.45537 | 0.77918 | 0.42254
I.E.S.J.VERNE | 0.086774 | 0.047056 | 0.07311 | 0.039647 | 0.06544 | 0.035487 | 0.060646 | 0.032887 | 0.057769 | 0.031327 | 0.053934 | 0.029247 | 0.049619 | 0.026908 | 0.043627 | 0.023658 | 0.046743 | 0.025348 | 0.051057 | 0.027688 | 0.061125 | 0.033147 | 0.063043 | 0.034187 | 0.07311 | 0.039647 | 0.093006 | 0.050436 | 0.11482 | 0.062265 | 0.12201 | 0.066164 | 0.11626 | 0.063044 | 0.11218 | 0.060835 | 0.10379 | 0.056285 | 0.097081 | 0.052645 | 0.083178 | 0.045106 | 0.091568 | 0.049656 | 0.10307 | 0.055895 | 0.095643 | 0.051865
ESTRELLA.ALTAIR | 0.453 | 0.24565 | 0.38167 | 0.20697 | 0.34162 | 0.18526 | 0.3166 | 0.17169 | 0.30158 | 0.16354 | 0.28156 | 0.15268 | 0.25903 | 0.14047 | 0.22775 | 0.1235 | 0.24402 | 0.13233 | 0.26654 | 0.14454 | 0.3191 | 0.17304 | 0.32911 | 0.17847 | 0.38167 | 0.20697 | 0.48553 | 0.2633 | 0.59941 | 0.32505 | 0.63695 | 0.34541 | 0.60692 | 0.32912 | 0.58564 | 0.31758 | 0.54184 | 0.29383 | 0.50681 | 0.27483 | 0.43423 | 0.23547 | 0.47802 | 0.25922 | 0.53809 | 0.2918 | 0.4993 | 0.27076
AGRICULTORES | 0.43803 | 0.23754 | 0.36906 | 0.20013 | 0.33034 | 0.17914 | 0.30614 | 0.16601 | 0.29162 | 0.15814 | 0.27226 | 0.14764 | 0.25048 | 0.13583 | 0.22023 | 0.11942 | 0.23596 | 0.12795 | 0.25774 | 0.13977 | 0.30856 | 0.16733 | 0.31824 | 0.17257 | 0.36906 | 0.20013 | 0.46949 | 0.2546 | 0.5796 | 0.31431 | 0.6159 | 0.33399 | 0.58686 | 0.31825 | 0.56629 | 0.30709 | 0.52394 | 0.28413 | 0.49006 | 0.26575 | 0.41988 | 0.22769 | 0.46223 | 0.25066 | 0.52031 | 0.28216 | 0.4828 | 0.26182
AGRICULTORES_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E.SIRIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 2.8937 |  | 2.438 |  | 2.1822 |  | 2.0224 |  | 1.9265 |  | 1.7986 |  | 1.6547 |  | 1.4548 |  | 1.5587 |  | 1.7026 |  | 2.0384 |  | 2.1023 |  | 2.438 |  | 3.1015 |  | 3.8289 |  | 4.0687 |  | 3.8769 |  | 3.741 |  | 3.4612 |  | 3.2374 |  | 2.7738 |  | 3.0535 |  | 3.4372 |  | 3.1894
LINEA EMPALME ESTRELLA SIRIO. AÑO 2
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
(MW y Mvar) | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q
E.SIRIO_1 | 0.29695 | 0.16103 | 0.2502 | 0.13568 | 0.22395 | 0.12144 | 0.20754 | 0.11255 | 0.1977 | 0.10721 | 0.18457 | 0.10009 | 0.1698 | 0.092082 | 0.1493 | 0.080961 | 0.15996 | 0.086744 | 0.17473 | 0.094751 | 0.20918 | 0.11343 | 0.21574 | 0.11699 | 0.2502 | 0.13568 | 0.31828 | 0.1726 | 0.39293 | 0.21308 | 0.41754 | 0.22642 | 0.39785 | 0.21575 | 0.38391 | 0.20819 | 0.3552 | 0.19262 | 0.33223 | 0.18016 | 0.28465 | 0.15436 | 0.31336 | 0.16993 | 0.35273 | 0.19128 | 0.32731 | 0.17749
E.SIRIO_2 | 0.97244 | 0.52734 | 0.81932 | 0.4443 | 0.73336 | 0.39769 | 0.67963 | 0.36855 | 0.6474 | 0.35107 | 0.60442 | 0.32776 | 0.55606 | 0.30154 | 0.48891 | 0.26513 | 0.52383 | 0.28406 | 0.57218 | 0.31028 | 0.685 | 0.37147 | 0.7065 | 0.38312 | 0.81932 | 0.4443 | 1.0423 | 0.56521 | 1.2867 | 0.69777 | 1.3673 | 0.74148 | 1.3029 | 0.70652 | 1.2572 | 0.68175 | 1.1632 | 0.63077 | 1.0879 | 0.58998 | 0.93214 | 0.50549 | 1.0262 | 0.55647 | 1.1551 | 0.62639 | 1.0718 | 0.58124
E.SIRIO_3 | 0.74227 | 0.40252 | 0.6254 | 0.33914 | 0.55978 | 0.30356 | 0.51877 | 0.28132 | 0.49417 | 0.26798 | 0.46136 | 0.25019 | 0.42445 | 0.23017 | 0.37319 | 0.20237 | 0.39984 | 0.21683 | 0.43675 | 0.23684 | 0.52287 | 0.28355 | 0.53928 | 0.29244 | 0.6254 | 0.33914 | 0.79559 | 0.43143 | 0.98218 | 0.53262 | 1.0437 | 0.56598 | 0.99448 | 0.53929 | 0.95962 | 0.52039 | 0.88786 | 0.48147 | 0.83044 | 0.45034 | 0.71152 | 0.38584 | 0.78328 | 0.42476 | 0.88171 | 0.47813 | 0.81814 | 0.44366
I.E.S.J.VERNE | 0.091112 | 0.049409 | 0.076766 | 0.041629 | 0.068712 | 0.037261 | 0.063678 | 0.034531 | 0.060658 | 0.032894 | 0.056631 | 0.03071 | 0.0521 | 0.028253 | 0.045808 | 0.024841 | 0.04908 | 0.026615 | 0.05361 | 0.029072 | 0.064181 | 0.034804 | 0.066195 | 0.035896 | 0.076766 | 0.041629 | 0.097656 | 0.052957 | 0.12056 | 0.065378 | 0.12811 | 0.069472 | 0.12207 | 0.066197 | 0.11779 | 0.063876 | 0.10898 | 0.059099 | 0.10194 | 0.055278 | 0.087337 | 0.047361 | 0.096146 | 0.052138 | 0.10823 | 0.05869 | 0.10042 | 0.054459
ESTRELLA.ALTAIR | 0.47565 | 0.25794 | 0.40075 | 0.21732 | 0.35871 | 0.19452 | 0.33243 | 0.18027 | 0.31666 | 0.17172 | 0.29564 | 0.16032 | 0.27199 | 0.14749 | 0.23914 | 0.12968 | 0.25622 | 0.13894 | 0.27987 | 0.15177 | 0.33506 | 0.18169 | 0.34557 | 0.1874 | 0.40075 | 0.21732 | 0.50981 | 0.27646 | 0.62938 | 0.3413 | 0.6688 | 0.36268 | 0.63726 | 0.34558 | 0.61492 | 0.33346 | 0.56894 | 0.30852 | 0.53215 | 0.28857 | 0.45594 | 0.24725 | 0.50193 | 0.27219 | 0.56499 | 0.30639 | 0.52426 | 0.2843
AGRICULTORES | 0.45993 | 0.24941 | 0.38751 | 0.21014 | 0.34685 | 0.18809 | 0.32144 | 0.17431 | 0.3062 | 0.16605 | 0.28587 | 0.15502 | 0.263 | 0.14262 | 0.23124 | 0.1254 | 0.24775 | 0.13435 | 0.27062 | 0.14675 | 0.32398 | 0.17569 | 0.33415 | 0.1812 | 0.38751 | 0.21014 | 0.49297 | 0.26733 | 0.60858 | 0.33002 | 0.6467 | 0.35069 | 0.61621 | 0.33416 | 0.59461 | 0.32245 | 0.55014 | 0.29833 | 0.51456 | 0.27904 | 0.44087 | 0.23908 | 0.48534 | 0.26319 | 0.54633 | 0.29626 | 0.50694 | 0.27491
AGRICULTORES_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E.SIRIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 3.0384 |  | 2.5599 |  | 2.2914 |  | 2.1235 |  | 2.0228 |  | 1.8885 |  | 1.7374 |  | 1.5276 |  | 1.6367 |  | 1.7878 |  | 2.1403 |  | 2.2074 |  | 2.5599 |  | 3.2566 |  | 4.0204 |  | 4.2722 |  | 4.0707 |  | 3.928 |  | 3.6343 |  | 3.3993 |  | 2.9125 |  | 3.2062 |  | 3.6091 |  | 3.3489
LINEA EMPALME ESTRELLA SIRIO. AÑO 3
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
(MW y Mvar) | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q | P | Q
E.SIRIO_1 | 0.3118 | 0.16908 | 0.26271 | 0.14246 | 0.23514 | 0.12751 | 0.21792 | 0.11817 | 0.20758 | 0.11257 | 0.1938 | 0.10509 | 0.1783 | 0.096687 | 0.15676 | 0.085009 | 0.16796 | 0.091082 | 0.18346 | 0.099489 | 0.21964 | 0.11911 | 0.22653 | 0.12284 | 0.26271 | 0.14246 | 0.3342 | 0.18123 | 0.41258 | 0.22373 | 0.43842 | 0.23775 | 0.41774 | 0.22654 | 0.4031 | 0.2186 | 0.37296 | 0.20225 | 0.34884 | 0.18917 | 0.29888 | 0.16208 | 0.32903 | 0.17843 | 0.37037 | 0.20085 | 0.34367 | 0.18637
E.SIRIO_2 | 1.0211 | 0.5537 | 0.86029 | 0.46652 | 0.77003 | 0.41757 | 0.71361 | 0.38698 | 0.67977 | 0.36863 | 0.63464 | 0.34415 | 0.58387 | 0.31662 | 0.51335 | 0.27838 | 0.55002 | 0.29827 | 0.60079 | 0.3258 | 0.71926 | 0.39004 | 0.74182 | 0.40228 | 0.86029 | 0.46652 | 1.0944 | 0.59347 | 1.3511 | 0.73266 | 1.4357 | 0.77855 | 1.368 | 0.74184 | 1.32 | 0.71584 | 1.2213 | 0.6623 | 1.1423 | 0.61948 | 0.97875 | 0.53076 | 1.0775 | 0.5843 | 1.2129 | 0.65771 | 1.1254 | 0.6103
E.SIRIO_3 | 0.77939 | 0.42265 | 0.65667 | 0.3561 | 0.58777 | 0.31874 | 0.54471 | 0.29539 | 0.51887 | 0.28138 | 0.48443 | 0.2627 | 0.44567 | 0.24168 | 0.39185 | 0.21249 | 0.41984 | 0.22767 | 0.45859 | 0.24869 | 0.54902 | 0.29772 | 0.56624 | 0.30706 | 0.65667 | 0.3561 | 0.83537 | 0.453 | 1.0313 | 0.55925 | 1.0959 | 0.59428 | 1.0442 | 0.56626 | 1.0076 | 0.54641 | 0.93225 | 0.50554 | 0.87197 | 0.47285 | 0.74709 | 0.40514 | 0.82245 | 0.446 | 0.92579 | 0.50204 | 0.85905 | 0.46585
I.E.S.J.VERNE | 0.095668 | 0.051879 | 0.080604 | 0.04371 | 0.072147 | 0.039124 | 0.066862 | 0.036258 | 0.063691 | 0.034538 | 0.059462 | 0.032245 | 0.054705 | 0.029666 | 0.048098 | 0.026083 | 0.051534 | 0.027946 | 0.056291 | 0.030526 | 0.06739 | 0.036545 | 0.069505 | 0.037691 | 0.080604 | 0.04371 | 0.10254 | 0.055605 | 0.12659 | 0.068647 | 0.13452 | 0.072946 | 0.12817 | 0.069507 | 0.12368 | 0.06707 | 0.11443 | 0.062054 | 0.10703 | 0.058042 | 0.091704 | 0.049729 | 0.10095 | 0.054745 | 0.11364 | 0.061624 | 0.10545 | 0.057182
ESTRELLA.ALTAIR | 0.49943 | 0.27083 | 0.42079 | 0.22819 | 0.37664 | 0.20425 | 0.34905 | 0.18928 | 0.33249 | 0.18031 | 0.31042 | 0.16833 | 0.28559 | 0.15487 | 0.25109 | 0.13616 | 0.26903 | 0.14589 | 0.29386 | 0.15936 | 0.35181 | 0.19078 | 0.36284 | 0.19676 | 0.42079 | 0.22819 | 0.5353 | 0.29028 | 0.66085 | 0.35837 | 0.70224 | 0.38081 | 0.66912 | 0.36286 | 0.64567 | 0.35014 | 0.59738 | 0.32395 | 0.55875 | 0.303 | 0.47873 | 0.25961 | 0.52702 | 0.2858 | 0.59324 | 0.32171 | 0.55048 | 0.29851
AGRICULTORES | 0.48293 | 0.26188 | 0.40689 | 0.22065 | 0.3642 | 0.1975 | 0.33752 | 0.18303 | 0.32151 | 0.17435 | 0.30016 | 0.16277 | 0.27615 | 0.14975 | 0.2428 | 0.13167 | 0.26014 | 0.14107 | 0.28415 | 0.15409 | 0.34018 | 0.18448 | 0.35086 | 0.19026 | 0.40689 | 0.22065 | 0.51761 | 0.28069 | 0.63901 | 0.34653 | 0.67903 | 0.36823 | 0.64702 | 0.35087 | 0.62434 | 0.33857 | 0.57765 | 0.31325 | 0.54029 | 0.29299 | 0.46292 | 0.25103 | 0.50961 | 0.27635 | 0.57364 | 0.31108 | 0.53229 | 0.28865
AGRICULTORES_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E.SIRIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.1903 |  | 2.6879 |  | 2.4059 |  | 2.2297 |  | 2.1239 |  | 1.9829 |  | 1.8243 |  | 1.6039 |  | 1.7185 |  | 1.8772 |  | 2.2473 |  | 2.3178 |  | 2.6879 |  | 3.4194 |  | 4.2214 |  | 4.4858 |  | 4.2743 |  | 4.1244 |  | 3.816 |  | 3.5692 |  | 3.0581 |  | 3.3665 |  | 3.7896 |  | 3.5164
Totales línea "Empalme-Corral del Acabose" (MWh) | [5 empty] | Totales línea "Empalme-E.Sirio"(MWh)
HORA | AÑO 0 | AÑO 1 | AÑO 2 | AÑO 3 |  | HORA | AÑO 0 | AÑO 1 | AÑO 2 | AÑO 3
1 | 2.174 | 2.2826 | 2.3968 | 2.5166 |  | 1 | 2.7559 | 2.8937 | 3.0384 | 3.1903
2 | 1.7483 | 1.8357 | 1.9275 | 2.0239 |  | 2 | 2.3219 | 2.438 | 2.5599 | 2.6879
3 | 1.505 | 1.5803 | 1.6593 | 1.7423 |  | 3 | 2.0783 | 2.1822 | 2.2914 | 2.4059
4 | 1.3454 | 1.4127 | 1.4833 | 1.5575 |  | 4 | 1.9261 | 2.0224 | 2.1235 | 2.2297
5 | 1.2618 | 1.3249 | 1.3911 | 1.4607 |  | 5 | 1.8347 | 1.9265 | 2.0228 | 2.1239
6 | 1.1706 | 1.2291 | 1.2906 | 1.3551 |  | 6 | 1.7129 | 1.7986 | 1.8885 | 1.9829
7 | 1.1326 | 1.1892 | 1.2487 | 1.3111 |  | 7 | 1.5759 | 1.6547 | 1.7374 | 1.8243
8 | 1.1858 | 1.2451 | 1.3073 | 1.3727 |  | 8 | 1.3856 | 1.4548 | 1.5276 | 1.6039
9 | 1.3758 | 1.4446 | 1.5168 | 1.5927 |  | 9 | 1.4845 | 1.5587 | 1.6367 | 1.7185
10 | 1.6039 | 1.6841 | 1.7683 | 1.8567 |  | 10 | 1.6216 | 1.7026 | 1.7878 | 1.8772
11 | 1.7939 | 1.8836 | 1.9778 | 2.0767 |  | 11 | 1.9413 | 2.0384 | 2.1403 | 2.2473
12 | 2.0979 | 2.2028 | 2.313 | 2.4286 |  | 12 | 2.0022 | 2.1023 | 2.2074 | 2.3178
13 | 2.3564 | 2.4742 | 2.5979 | 2.7278 |  | 13 | 2.3219 | 2.438 | 2.5599 | 2.6879
14 | 2.9417 | 3.0888 | 3.2432 | 3.4054 |  | 14 | 2.9538 | 3.1015 | 3.2566 | 3.4194
15 | 3.5498 | 3.7273 | 3.9136 | 4.1093 |  | 15 | 3.6466 | 3.8289 | 4.0204 | 4.2214
16 | 3.907 | 4.1024 | 4.3075 | 4.5229 |  | 16 | 3.875 | 4.0687 | 4.2722 | 4.4858
17 | 3.5346 | 3.7113 | 3.8969 | 4.0917 |  | 17 | 3.6923 | 3.8769 | 4.0707 | 4.2743
18 | 3.4054 | 3.5756 | 3.7544 | 3.9421 |  | 18 | 3.5628 | 3.741 | 3.928 | 4.1244
19 | 3.2989 | 3.4639 | 3.6371 | 3.8189 |  | 19 | 3.2964 | 3.4612 | 3.6343 | 3.816
20 | 2.8353 | 2.977 | 3.1259 | 3.2822 |  | 20 | 3.0832 | 3.2374 | 3.3993 | 3.5692
21 | 2.516 | 2.6418 | 2.7739 | 2.9126 |  | 21 | 2.6417 | 2.7738 | 2.9125 | 3.0581
22 | 2.5768 | 2.7057 | 2.8409 | 2.983 |  | 22 | 2.9081 | 3.0535 | 3.2062 | 3.3665
23 | 2.7668 | 2.9052 | 3.0505 | 3.203 |  | 23 | 3.2736 | 3.4372 | 3.6091 | 3.7896
24 | 2.5616 | 2.6897 | 2.8242 | 2.9654 |  | 24 | 3.0376 | 3.1894 | 3.3489 | 3.5164
Total (MWh) | 54.6453 | 57.3775 | 60.2464 | 63.2587 |  | Total | 60.9338 | 63.9805 | 67.1796 | 70.5385
Total | 115.5791 | 121.3581 | 127.426 | 133.7973
HORA | AÑO 3 | Media
1 | 5.7069 | 5.5749 | 0.13201
2 | 4.7118 | 5.5749 |  | -0.86309
3 | 4.1482 | 5.5749 |  | -1.4267
4 | 3.7872 | 5.5749 |  | -1.7877
5 | 3.5846 | 5.5749 |  | -1.9903
6 | 3.338 | 5.5749 |  | -2.2369
7 | 3.1354 | 5.5749 |  | -2.4395
8 | 2.9767 | 5.5749 |  | -2.5982
9 | 3.3112 | 5.5749 |  | -2.2637
10 | 3.7338 | 5.5749 |  | -1.8411
11 | 4.3239 | 5.5749 |  | -1.2509
12 | 4.7464 | 5.5749 |  | -0.82846
13 | 5.4157 | 5.5749 |  | -0.15914
14 | 6.8248 | 5.5749 | 1.2499
15 | 8.3307 | 5.5749 | 2.7558
16 | 9.0087 | 5.5749 | 3.4338
17 | 8.366 | 5.5749 | 2.7911
18 | 8.0666 | 5.5749 | 2.4917
19 | 7.6349 | 5.5749 | 2.06
20 | 6.8514 | 5.5749 | 1.2765
21 | 5.9707 | 5.5749 | 0.39579
22 | 6.3495 | 5.5749 | 0.77463
23 | 6.9925 | 5.5749 | 1.4176
24 | 6.4817 | 5.5749 | 0.90686

## PERDIDAS
PERDIDAS AÑO 1 | [8 empty] | PERDIDAS AÑO 1 | [8 empty] | PERDIDAS AÑO 1 | [8 empty] | PERDIDAS AÑO 1 | [8 empty] | PERDIDAS AÑO 1
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
TRAFO | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
| 0.0021 | 0.0356 | 0.0015 | 0.0245 | 0.0011 | 0.0186 | 0.0009 | 0.0155 | 0.0008 | 0.0139 | 0.0007 | 0.012 | 0.0006 | 0.0106 | 0.0006 | 0.0096 | 0.0007 | 0.0116 | 0.0009 | 0.0151 | 0.0012 | 0.0203 | 0.0015 | 0.0245 | 0.0019 | 0.0319 | 0.0031 | 0.0511 | 0.0046 | 0.0766 | 0.0054 | 0.0898 | 0.0046 | 0.0772 | 0.0043 | 0.0717 | 0.0039 | 0.0641 | 0.0031 | 0.0515 | 0.0031 | 0.0515 | 0.0026 | 0.044 | 0.0032 | 0.0536 | 0.0028 | 0.046
| 0.0021 |  | 0.0015 |  | 0.0011 |  | 0.0009 |  | 0.0008 |  | 0.0007 |  | 0.0006 |  | 0.0006 |  | 0.0007 |  | 0.0009 |  | 0.0012 |  | 0.0015 |  | 0.0019 |  | 0.0031 |  | 0.0046 |  | 0.0054 |  | 0.0046 |  | 0.0043 |  | 0.0039 |  | 0.0031 |  | 0.0031 |  | 0.0026 |  | 0.0032 |  | 0.0028
LINEA EMPALME-CORRAL DEL ACABOSE AÑO 1
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
| MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
EMPAL-CRAL.ACABOSE_1 | 0.0136 | 0.0114 | 0.0088 | 0.0073 | 0.0065 | 0.0054 | 0.0052 | 0.0043 | 0.0045 | 0.0038 | 0.0039 | 0.0033 | 0.0037 | 0.0031 | 0.004 | 0.0033 | 0.0054 | 0.0045 | 0.0073 | 0.0061 | 0.0092 | 0.0077 | 0.0126 | 0.0105 | 0.0159 | 0.0133 | 0.025 | 0.0209 | 0.0367 | 0.0307 | 0.0445 | 0.0373 | 0.0364 | 0.0304 | 0.0337 | 0.0282 | 0.0316 | 0.0264 | 0.0232 | 0.0194 | 0.0232 | 0.0194 | 0.0192 | 0.016 | 0.0221 | 0.0185 | 0.0189 | 0.0159
CRAL ACABOSE_1-CRAL.ACABOSE_2 | 0.0005 | 0.0004 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0006 | 0.0005 | 0.001 | 0.0008 | 0.0014 | 0.0012 | 0.0017 | 0.0014 | 0.0014 | 0.0012 | 0.0013 | 0.0011 | 0.0012 | 0.001 | 0.0009 | 0.0007 | 0.0009 | 0.0007 | 0.0007 | 0.0006 | 0.0008 | 0.0007 | 0.0007 | 0.0006
CRAL ACABOSE_2-E.SIRIO_4 | 0.0004 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0008 | 0.0006 | 0.0012 | 0.0009 | 0.0014 | 0.0011 | 0.0012 | 0.0009 | 0.0011 | 0.0009 | 0.001 | 0.0008 | 0.0007 | 0.0006 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0007 | 0.0006 | 0.0006 | 0.0005
SUBTOTAL PERDIDAS | 0.0145 | 0.0121 | 0.0094 | 0.0078 | 0.0069 | 0.0058 | 0.0056 | 0.0046 | 0.0048 | 0.004 | 0.0041 | 0.0035
| 0.0145 |  | 0.0094 |  | 0.0069 |  | 0.0056 |  | 0.0048 |  | 0.0041 |  | 0.0039 |  | 0.0043 |  | 0.0058 |  | 0.0078 |  | 0.0099 |  | 0.0135 |  | 0.017 |  | 0.0268 |  | 0.0393 |  | 0.0476 |  | 0.039 |  | 0.0361 |  | 0.0338 |  | 0.0248 |  | 0.0248 |  | 0.0205 |  | 0.0236 |  | 0.0202
LINEA EMPALME ESTRELLA SIRIO. AÑO 1
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
(MW y Mvar) | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
E.SIRIO_1 | 0.031 | 0.0259 | 0.0226 | 0.0188 | 0.0175 | 0.0146 | 0.015 | 0.0126 | 0.0136 | 0.0114 | 0.0119 | 0.0099 | 0.01 | 0.0084 | 0.0077 | 0.0065 | 0.0086 | 0.0072 | 0.0106 | 0.0089 | 0.0153 | 0.0128 | 0.0163 | 0.0136 | 0.022 | 0.0184 | 0.0358 | 0.0299 | 0.0549 | 0.0458 | 0.0622 | 0.0519 | 0.0563 | 0.047 | 0.0524 | 0.0437 | 0.0447 | 0.0374 | 0.039 | 0.0326 | 0.039 | 0.0326 | 0.0345 | 0.0288 | 0.044 | 0.0368 | 0.0378 | 0.0316
E.SIRIO_2 | 0.0011 | 0.0009 | 0.0008 | 0.0006 | 0.0006 | 0.0005 | 0.0005 | 0.0004 | 0.0005 | 0.0004 | 0.0004 | 0.0003 | 0.0004 | 0.0003 | 0.0003 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0006 | 0.0005 | 0.0008 | 0.0006 | 0.0013 | 0.001 | 0.0019 | 0.0016 | 0.0022 | 0.0018 | 0.002 | 0.0016 | 0.0018 | 0.0015 | 0.0016 | 0.0013 | 0.0014 | 0.0011 | 0.0014 | 0.0011 | 0.0012 | 0.001 | 0.0015 | 0.0013 | 0.0013 | 0.0011
E.SIRIO_3 | 0.0014 | 0.0012 | 0.001 | 0.0008 | 0.0008 | 0.0007 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0005 | 0.0004 | 0.0005 | 0.0004 | 0.0003 | 0.0003 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0007 | 0.0006 | 0.0007 | 0.0006 | 0.001 | 0.0008 | 0.0016 | 0.0013 | 0.0025 | 0.0021 | 0.0028 | 0.0023 | 0.0025 | 0.0021 | 0.0024 | 0.002 | 0.002 | 0.0017 | 0.0018 | 0.0015 | 0.0018 | 0.0015 | 0.0016 | 0.0013 | 0.002 | 0.0017 | 0.0017 | 0.0014
I.E.S.J.VERNE | 0.0006 | 0.0005 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0003 | 0.0002 | 0.0004 | 0.0003 | 0.0006 | 0.0005 | 0.001 | 0.0008 | 0.0011 | 0.0009 | 0.001 | 0.0009 | 0.0009 | 0.0008 | 0.0008 | 0.0007 | 0.0007 | 0.0006 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0008 | 0.0007 | 0.0007 | 0.0006
ESTRELLA.ALTAIR | 0.0005 | 0.0005 | 0.0003 | 0.0004 | 0.0003 | 0.0003 | 0.0002 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0001 | 0.0001 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0005 | 0.0006 | 0.0008 | 0.001 | 0.001 | 0.0011 | 0.0009 | 0.001 | 0.0008 | 0.0009 | 0.0007 | 0.0008 | 0.0006 | 0.0007 | 0.0006 | 0.0007 | 0.0005 | 0.0006 | 0.0007 | 0.0008 | 0.0006 | 0.0007
AGRICULTORES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AGRICULTORES_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E.SIRIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUBTOTAL PERDIDAS | 0.0346 |  | 0.0251 |  | 0.0195 |  | 0.0167 |  | 0.0151 |  | 0.0132 |  | 0.0113 |  | 0.0085 |  | 0.0096 |  | 0.0119 |  | 0.017 |  | 0.0181 |  | 0.0245 |  | 0.0398 |  | 0.0611 |  | 0.0693 |  | 0.0627 |  | 0.0583 |  | 0.0498 |  | 0.0435 |  | 0.0435 |  | 0.0384 |  | 0.049 |  | 0.0421
PERDIDAS AÑO 2 | [8 empty] | PERDIDAS AÑO 2 | [8 empty] | PERDIDAS AÑO 2 | [8 empty] | PERDIDAS AÑO 2 | [8 empty] | PERDIDAS AÑO 2 | [8 empty] | PERDIDAS AÑO 2
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
TRAFO | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
| 0.0024 | 0.0392 | 0.0016 | 0.0266 | 0.0013 | 0.021 | 0.0011 | 0.0175 | 0.0009 | 0.0153 | 0.0008 | 0.0133 | 0.0007 | 0.0111 | 0.0006 | 0.0105 | 0.0008 | 0.0131 | 0.001 | 0.0166 | 0.0013 | 0.0223 | 0.0016 | 0.0269 | 0.0021 | 0.0353 | 0.0034 | 0.0564 | 0.0051 | 0.0846 | 0.006 | 0.0992 | 0.0051 | 0.0853 | 0.0048 | 0.0792 | 0.0043 | 0.0708 | 0.0034 | 0.0565 | 0.0026 | 0.043 | 0.0029 | 0.0487 | 0.0036 | 0.0593 | 0.0031 | 0.0508
| 0.0024 |  | 0.0016 |  | 0.0013 |  | 0.0011 |  | 0.0009 |  | 0.0008 |  | 0.0007 |  | 0.0006 |  | 0.0008 |  | 0.001 |  | 0.0013 |  | 0.0016 |  | 0.0021 |  | 0.0034 |  | 0.0051 |  | 0.006 |  | 0.0051 |  | 0.0048 |  | 0.0043 |  | 0.0034 |  | 0.0026 |  | 0.0029 |  | 0.0036 |  | 0.0031
LINEA EMPALME-CORRAL DEL ACABOSE AÑO 2 | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 2 | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 2 | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 2 | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 2
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
| MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
EMPAL-CRAL.ACABOSE_1 | 0.015 | 0.0126 | 0.0097 | 0.0081 | 0.0075 | 0.0063 | 0.006 | 0.005 | 0.005 | 0.0042 | 0.0043 | 0.0036 | 0.004 | 0.0034 | 0.0044 | 0.0037 | 0.0059 | 0.005 | 0.0081 | 0.0068 | 0.01 | 0.0084 | 0.0138 | 0.0116 | 0.0176 | 0.0147 | 0.0276 | 0.0231 | 0.0405 | 0.0339 | 0.0492 | 0.0412 | 0.0402 | 0.0336 | 0.0372 | 0.0311 | 0.0349 | 0.0292 | 0.0255 | 0.0213 | 0.0201 | 0.0168 | 0.0212 | 0.0177 | 0.0245 | 0.0205 | 0.0209 | 0.0175
CRAL ACABOSE_1-CRAL.ACABOSE_2 | 0.0006 | 0.0005 | 0.0004 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0007 | 0.0006 | 0.0011 | 0.0009 | 0.0016 | 0.0013 | 0.0019 | 0.0016 | 0.0015 | 0.0013 | 0.0014 | 0.0012 | 0.0013 | 0.0011 | 0.001 | 0.0008 | 0.0008 | 0.0006 | 0.0008 | 0.0007 | 0.0009 | 0.0008 | 0.0008 | 0.0007
CRAL ACABOSE_2-E.SIRIO_4 | 0.0005 | 0.0004 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0004 | 0.0006 | 0.0004 | 0.0009 | 0.0007 | 0.0013 | 0.001 | 0.0016 | 0.0013 | 0.0013 | 0.001 | 0.0012 | 0.0009 | 0.0011 | 0.0009 | 0.0008 | 0.0007 | 0.0006 | 0.0005 | 0.0007 | 0.0005 | 0.0008 | 0.0006 | 0.0007 | 0.0005
SUBTOTAL PERDIDAS | 0.0161 |  | 0.0104 |  | 0.008 |  | 0.0064 |  | 0.0054 |  | 0.0046 |  | 0.0043 |  | 0.0047 |  | 0.0063 |  | 0.0087 |  | 0.0107 |  | 0.0147 |  | 0.0189 |  | 0.0296 |  | 0.0434 |  | 0.0527 |  | 0.043 |  | 0.0398 |  | 0.0373 |  | 0.0273 |  | 0.0215 |  | 0.0227 |  | 0.0262 |  | 0.0224
LINEA EMPALME ESTRELLA SIRIO. AÑO 2 | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 2 | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 2 | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 2 | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 2
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
(MW y Mvar) | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
E.SIRIO_1 | 0.0342 | 0.0286 | 0.0242 | 0.0202 | 0.0194 | 0.0162 | 0.0166 | 0.0139 | 0.015 | 0.0126 | 0.0131 | 0.0109 | 0.01 | 0.0084 | 0.0085 | 0.0071 | 0.0098 | 0.0082 | 0.0118 | 0.0098 | 0.0169 | 0.0141 | 0.018 | 0.015 | 0.0243 | 0.0203 | 0.0395 | 0.033 | 0.0607 | 0.0507 | 0.0687 | 0.0574 | 0.0622 | 0.0519 | 0.0578 | 0.0483 | 0.0494 | 0.0412 | 0.0429 | 0.0358 | 0.0315 | 0.0263 | 0.0382 | 0.0319 | 0.0486 | 0.0406 | 0.0417 | 0.0348
E.SIRIO_2 | 0.0012 | 0.001 | 0.0008 | 0.0007 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0005 | 0.0004 | 0.0005 | 0.0004 | 0.0004 | 0.0003 | 0.0003 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0003 | 0.0006 | 0.0005 | 0.0006 | 0.0005 | 0.0008 | 0.0007 | 0.0014 | 0.0012 | 0.0021 | 0.0018 | 0.0024 | 0.002 | 0.0022 | 0.0018 | 0.002 | 0.0017 | 0.0017 | 0.0014 | 0.0015 | 0.0013 | 0.0011 | 0.0009 | 0.0013 | 0.0011 | 0.0017 | 0.0014 | 0.0015 | 0.0012
E.SIRIO_3 | 0.0015 | 0.0013 | 0.0011 | 0.0009 | 0.0009 | 0.0007 | 0.0007 | 0.0006 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0005 | 0.0004 | 0.0004 | 0.0003 | 0.0004 | 0.0004 | 0.0005 | 0.0004 | 0.0008 | 0.0006 | 0.0008 | 0.0007 | 0.0011 | 0.0009 | 0.0018 | 0.0015 | 0.0027 | 0.0023 | 0.0031 | 0.0026 | 0.0028 | 0.0023 | 0.0026 | 0.0022 | 0.0022 | 0.0019 | 0.0019 | 0.0016 | 0.0014 | 0.0012 | 0.0017 | 0.0014 | 0.0022 | 0.0018 | 0.0019 | 0.0016
I.E.S.J.VERNE | 0.0006 | 0.0005 | 0.0004 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0004 | 0.0004 | 0.0007 | 0.0006 | 0.0011 | 0.0009 | 0.0012 | 0.001 | 0.0011 | 0.0009 | 0.001 | 0.0009 | 0.0009 | 0.0007 | 0.0008 | 0.0007 | 0.0006 | 0.0005 | 0.0007 | 0.0006 | 0.0009 | 0.0007 | 0.0008 | 0.0006
ESTRELLA.ALTAIR | 0.0005 | 0.0006 | 0.0004 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0004 | 0.0004 | 0.0006 | 0.0007 | 0.0009 | 0.0011 | 0.0011 | 0.0012 | 0.001 | 0.0011 | 0.0009 | 0.001 | 0.0008 | 0.0009 | 0.0007 | 0.0008 | 0.0005 | 0.0006 | 0.0006 | 0.0007 | 0.0007 | 0.0009 | 0.0006 | 0.0007
AGRICULTORES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AGRICULTORES_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E.SIRIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUBTOTAL PERDIDAS | 0.038 |  | 0.0269 |  | 0.0216 |  | 0.0185 |  | 0.0167 |  | 0.0146 |  | 0.0113 |  | 0.0095 |  | 0.0109 |  | 0.0131 |  | 0.0189 |  | 0.02 |  | 0.027 |  | 0.044 |  | 0.0675 |  | 0.0765 |  | 0.0693 |  | 0.0643 |  | 0.055 |  | 0.0478 |  | 0.0351 |  | 0.0425 |  | 0.0541 |  | 0.0465
PERDIDAS AÑO 3 | [8 empty] | PERDIDAS AÑO 3 | [8 empty] | PERDIDAS AÑO 3 | [8 empty] | PERDIDAS AÑO 3 | [8 empty] | PERDIDAS AÑO 3 | [8 empty] | PERDIDAS AÑO 3
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
TRAFO | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
| 0.0026 | 0.0433 | 0.0018 | 0.0294 | 0.0014 | 0.0227 | 0.0011 | 0.0188 | 0.001 | 0.0169 | 0.0009 | 0.0147 | 0.0008 | 0.0129 | 0.0007 | 0.0116 | 0.0009 | 0.0144 | 0.0011 | 0.018 | 0.0015 | 0.0247 | 0.0018 | 0.0301 | 0.0024 | 0.0393 | 0.0037 | 0.0622 | 0.0056 | 0.0935 | 0.0066 | 0.1096 | 0.0057 | 0.0943 | 0.0052 | 0.086 | 0.0047 | 0.0782 | 0.0038 | 0.0627 | 0.0029 | 0.0475 | 0.0032 | 0.0538 | 0.0039 | 0.0655 | 0.0034 | 0.0561
| 0.0026 |  | 0.0018 |  | 0.0014 |  | 0.0011 |  | 0.001 |  | 0.0009 |  | 0.0008 |  | 0.0007 |  | 0.0009 |  | 0.0011 |  | 0.0015 |  | 0.0018 |  | 0.0024 |  | 0.0037 |  | 0.0056 |  | 0.0066 |  | 0.0057 |  | 0.0052 |  | 0.0047 |  | 0.0038 |  | 0.0029 |  | 0.0032 |  | 0.0039 |  | 0.0034
LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
| MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
EMPAL-CRAL.ACABOSE_1 | 0.0166 | 0.0139 | 0.0107 | 0.0089 | 0.0079 | 0.0066 | 0.0063 | 0.0053 | 0.0055 | 0.0046 | 0.0048 | 0.004 | 0.0044 | 0.0037 | 0.0049 | 0.0041 | 0.0066 | 0.0055 | 0.0086 | 0.0072 | 0.0112 | 0.0094 | 0.0156 | 0.0131 | 0.0194 | 0.0163 | 0.0305 | 0.0255 | 0.0447 | 0.0374 | 0.0544 | 0.0455 | 0.0444 | 0.0371 | 0.0397 | 0.0332 | 0.0385 | 0.0322 | 0.0283 | 0.0237 | 0.0222 | 0.0186 | 0.0234 | 0.0195 | 0.027 | 0.0226 | 0.0231 | 0.0193
CRAL ACABOSE_1-CRAL.ACABOSE_2 | 0.0006 | 0.0005 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0004 | 0.0006 | 0.0005 | 0.0007 | 0.0006 | 0.0012 | 0.001 | 0.0017 | 0.0014 | 0.0021 | 0.0017 | 0.0017 | 0.0014 | 0.0015 | 0.0013 | 0.0015 | 0.0012 | 0.0011 | 0.0009 | 0.0009 | 0.0007 | 0.0009 | 0.0007 | 0.001 | 0.0009 | 0.0009 | 0.0007
CRAL ACABOSE_2-E.SIRIO_4 | 0.0005 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0002 | 0.0001 | 0.0001 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0006 | 0.0005 | 0.001 | 0.0008 | 0.0014 | 0.0011 | 0.0017 | 0.0014 | 0.0014 | 0.0011 | 0.0012 | 0.001 | 0.0012 | 0.001 | 0.0009 | 0.0007 | 0.0007 | 0.0006 | 0.0007 | 0.0006 | 0.0009 | 0.0007 | 0.0007 | 0.0006
SUBTOTAL PERDIDAS | 0.0177 |  | 0.0114 |  | 0.0085 |  | 0.0067 |  | 0.0059 |  | 0.0052 |  | 0.0047 |  | 0.0053 |  | 0.0071 |  | 0.0092 |  | 0.012 |  | 0.0167 |  | 0.0207 |  | 0.0327 |  | 0.0478 |  | 0.0582 |  | 0.0475 |  | 0.0424 |  | 0.0412 |  | 0.0303 |  | 0.0238 |  | 0.025 |  | 0.0289 |  | 0.0247
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
(MW y Mvar) | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
E.SIRIO_1 | 0.0378 | 0.0316 | 0.0267 | 0.0223 | 0.0214 | 0.0178 | 0.0182 | 0.0152 | 0.0166 | 0.0139 | 0.0144 | 0.0121 | 0.0122 | 0.0102 | 0.0094 | 0.0079 | 0.0108 | 0.0091 | 0.013 | 0.0108 | 0.0186 | 0.0155 | 0.0205 | 0.0171 | 0.0273 | 0.0228 | 0.0436 | 0.0364 | 0.067 | 0.056 | 0.0759 | 0.0634 | 0.0687 | 0.0574 | 0.0639 | 0.0534 | 0.0545 | 0.0455 | 0.0476 | 0.0397 | 0.0348 | 0.029 | 0.0422 | 0.0352 | 0.0537 | 0.0448 | 0.0461 | 0.0385
E.SIRIO_2 | 0.0013 | 0.0011 | 0.0009 | 0.0008 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0006 | 0.0005 | 0.0005 | 0.0004 | 0.0004 | 0.0004 | 0.0003 | 0.0003 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0007 | 0.0005 | 0.0007 | 0.0006 | 0.001 | 0.0008 | 0.0015 | 0.0013 | 0.0023 | 0.002 | 0.0027 | 0.0022 | 0.0024 | 0.002 | 0.0022 | 0.0019 | 0.0019 | 0.0016 | 0.0017 | 0.0014 | 0.0012 | 0.001 | 0.0015 | 0.0012 | 0.0019 | 0.0016 | 0.0016 | 0.0013
E.SIRIO_3 | 0.0017 | 0.0014 | 0.0012 | 0.001 | 0.001 | 0.0008 | 0.0008 | 0.0007 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0006 | 0.0005 | 0.0004 | 0.0004 | 0.0005 | 0.0004 | 0.0006 | 0.0005 | 0.0008 | 0.0007 | 0.0009 | 0.0008 | 0.0012 | 0.001 | 0.002 | 0.0016 | 0.003 | 0.0025 | 0.0034 | 0.0029 | 0.0031 | 0.0026 | 0.0029 | 0.0024 | 0.0025 | 0.0021 | 0.0021 | 0.0018 | 0.0016 | 0.0013 | 0.0019 | 0.0016 | 0.0024 | 0.002 | 0.0021 | 0.0017
I.E.S.J.VERNE | 0.0007 | 0.0006 | 0.0005 | 0.0004 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0008 | 0.0007 | 0.0012 | 0.001 | 0.0014 | 0.0011 | 0.0012 | 0.001 | 0.0012 | 0.001 | 0.001 | 0.0008 | 0.0009 | 0.0007 | 0.0006 | 0.0005 | 0.0008 | 0.0006 | 0.001 | 0.0008 | 0.0008 | 0.0007
ESTRELLA.ALTAIR | 0.0006 | 0.0007 | 0.0004 | 0.0005 | 0.0003 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0003 | 0.0002 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0003 | 0.0003 | 0.0003 | 0.0004 | 0.0004 | 0.0005 | 0.0007 | 0.0008 | 0.001 | 0.0012 | 0.0012 | 0.0013 | 0.0011 | 0.0012 | 0.001 | 0.0011 | 0.0008 | 0.001 | 0.0007 | 0.0008 | 0.0005 | 0.0006 | 0.0006 | 0.0007 | 0.0008 | 0.0009 | 0.0007 | 0.0008
AGRICULTORES | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AGRICULTORES_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E.SIRIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SUBTOTAL PERDIDAS | 0.0421 |  | 0.0297 |  | 0.0238 |  | 0.0202 |  | 0.0185 |  | 0.016 |  | 0.0136 |  | 0.0104 |  | 0.0121 |  | 0.0145 |  | 0.0207 |  | 0.0228 |  | 0.0304 |  | 0.0486 |  | 0.0745 |  | 0.0846 |  | 0.0765 |  | 0.0712 |  | 0.0607 |  | 0.053 |  | 0.0387 |  | 0.047 |  | 0.0598 |  | 0.0513
| 0.0765 |  | 0.0712 |  | 0.0607 |  | 0.053 |  | 0.0387 |  | 0.047 |  | 0.0598 |  | 0.0513
| AÑO 1 (MWh) |  |  |  | AÑO 2 (MWh) |  |  |  | AÑO 3 (MWh) |  |  |  | Pérdidas |  |  |  | Hora
HORA | TRAFO | E-C | E-ES | Total(kWh) | TRAFO | E-C | E-ES | Total (kWh) | TRAFO | E-C | E-ES | Total (kWh) | Año1 | Año2 | Año3 | Total(kWh)
1 | 0.0021 | 0.0145 | 0.0346 | 51.2 | 0.0024 | 0.0161 | 0.038 | 56.5 | 0.0026 | 0.0177 | 0.0421 | 62.4 | 10.11% | 21.51% | 34.19% | 46.5 | 1
2 | 0.0015 | 0.0094 | 0.0251 | 36 | 0.0016 | 0.0104 | 0.0269 | 38.9 | 0.0018 | 0.0114 | 0.0297 | 42.9 | 12.5% | 21.56% | 34.06% | 32 | 2
3 | 0.0011 | 0.0069 | 0.0195 | 27.5 | 0.0013 | 0.008 | 0.0216 | 30.9 | 0.0014 | 0.0085 | 0.0238 | 33.7 | 10% | 23.6% | 34.8% | 25 | 3
4 | 0.0009 | 0.0056 | 0.0167 | 23.2 | 0.0011 | 0.0064 | 0.0185 | 26 | 0.0011 | 0.0067 | 0.0202 | 28 | 11.54% | 25% | 34.62% | 20.8 | 4
5 | 0.0008 | 0.0048 | 0.0151 | 20.7 | 0.0009 | 0.0054 | 0.0167 | 23 | 0.001 | 0.0059 | 0.0185 | 25.4 | 7.812% | 19.79% | 32.29% | 19.2 | 5
6 | 0.0007 | 0.0041 | 0.0132 | 18 | 0.0008 | 0.0046 | 0.0146 | 20 | 0.0009 | 0.0052 | 0.016 | 22.1 | 12.5% | 25% | 38.12% | 16 | 6
7 | 0.0006 | 0.0039 | 0.0113 | 15.8 | 0.0007 | 0.0043 | 0.0113 | 16.3 | 0.0008 | 0.0047 | 0.0136 | 19.1 | 11.27% | 14.79% | 34.51% | 14.2 | 7
8 | 0.0006 | 0.0043 | 0.0085 | 13.4 | 0.0006 | 0.0047 | 0.0095 | 14.8 | 0.0007 | 0.0053 | 0.0104 | 16.4 | 11.67% | 23.33% | 36.67% | 12 | 8
9 | 0.0007 | 0.0058 | 0.0096 | 16.1 | 0.0008 | 0.0063 | 0.0109 | 18 | 0.0009 | 0.0071 | 0.0121 | 20.1 | 8.054% | 20.81% | 34.9% | 14.9 | 9
10 | 0.0009 | 0.0078 | 0.0119 | 20.6 | 0.001 | 0.0087 | 0.0131 | 22.8 | 0.0011 | 0.0092 | 0.0145 | 24.8 | 10.16% | 21.93% | 32.62% | 18.7 | 10
11 | 0.0012 | 0.0099 | 0.017 | 28.1 | 0.0013 | 0.0107 | 0.0189 | 30.9 | 0.0015 | 0.012 | 0.0207 | 34.2 | 11.51% | 22.62% | 35.71% | 25.2 | 11
12 | 0.0015 | 0.0135 | 0.0181 | 33.1 | 0.0016 | 0.0147 | 0.02 | 36.3 | 0.0018 | 0.0167 | 0.0228 | 41.3 | 9.603% | 20.2% | 36.75% | 30.2 | 12 |  |  | Pérdidas |  |  |  | Hora |  | Pérdidas
13 | 0.0019 | 0.017 | 0.0245 | 43.4 | 0.0021 | 0.0189 | 0.027 | 48 | 0.0024 | 0.0207 | 0.0304 | 53.5 | 9.873% | 21.52% | 35.44% | 39.5 | 13 |  |  | Año1 | Año2 | Año3 | Total(kWh) |  |  | Año1 | Año2 | Año3 | Total(kWh)
14 | 0.0031 | 0.0268 | 0.0398 | 69.7 | 0.0034 | 0.0296 | 0.044 | 77 | 0.0037 | 0.0327 | 0.0486 | 85 | 10.28% | 21.84% | 34.49% | 63.2 | 14 |  |  | 10.11% | 21.51% | 34.19% | 46.5 | 1 | 13 | 9.873% | 21.52% | 35.44% | 39.5
15 | 0.0046 | 0.0393 | 0.0611 | 105 | 0.0051 | 0.0434 | 0.0675 | 116 | 0.0056 | 0.0478 | 0.0745 | 127.9 | 11.58% | 23.27% | 35.92% | 94.1 | 15 |  |  | 12.5% | 21.56% | 34.06% | 32 | 2 | 14 | 10.28% | 21.84% | 34.49% | 63.2
16 | 0.0054 | 0.0476 | 0.0693 | 122.3 | 0.006 | 0.0527 | 0.0765 | 135.2 | 0.0066 | 0.0582 | 0.0846 | 149.4 | 19.42% | 32.02% | 45.88% | 102.41 | 16 |  |  | 10% | 23.6% | 34.8% | 25 | 3 | 15 | 11.58% | 23.27% | 35.92% | 94.1
17 | 0.0046 | 0.039 | 0.0627 | 106.3 | 0.0051 | 0.043 | 0.0693 | 117.4 | 0.0057 | 0.0475 | 0.0765 | 129.7 | 11.08% | 22.68% | 35.53% | 95.7 | 17 |  |  | 11.54% | 25% | 34.62% | 20.8 | 4 | 16 | 19.42% | 32.02% | 45.88% | 102.41
18 | 0.0043 | 0.0361 | 0.0583 | 98.7 | 0.0048 | 0.0398 | 0.0643 | 108.9 | 0.0052 | 0.0424 | 0.0712 | 118.8 | 10.16% | 21.54% | 32.59% | 89.6 | 18 |  |  | 7.812% | 19.79% | 32.29% | 19.2 | 5 | 17 | 11.08% | 22.68% | 35.53% | 95.7
19 | 0.0039 | 0.0338 | 0.0498 | 87.5 | 0.0043 | 0.0373 | 0.055 | 96.6 | 0.0047 | 0.0412 | 0.0607 | 106.6 | 10.06% | 21.51% | 34.09% | 79.5 | 19 |  |  | 12.5% | 25% | 38.12% | 16 | 6 | 18 | 10.16% | 21.54% | 32.59% | 89.6
20 | 0.0031 | 0.0248 | 0.0435 | 71.4 | 0.0034 | 0.0273 | 0.0478 | 78.5 | 0.0038 | 0.0303 | 0.053 | 87.1 | 10.36% | 21.33% | 34.62% | 64.7 | 20 |  |  | 11.27% | 14.79% | 34.51% | 14.2 | 7 | 19 | 10.06% | 21.51% | 34.09% | 79.5
21 | 0.00232 | 0.0195 | 0.0355 | 57.32 | 0.0026 | 0.0215 | 0.0351 | 59.2 | 0.0029 | 0.0238 | 0.0387 | 65.4 | 17.46% | 21.31% | 34.02% | 48.8 | 21 |  |  | 11.67% | 23.33% | 36.67% | 12 | 8 | 20 | 10.36% | 21.33% | 34.62% | 64.7
22 | 0.0026 | 0.0205 | 0.0384 | 61.5 | 0.0029 | 0.0227 | 0.0425 | 68.1 | 0.0032 | 0.025 | 0.047 | 75.2 | 9.626% | 21.39% | 34.05% | 56.1 | 22 |  |  | 8.054% | 20.81% | 34.9% | 14.9 | 9 | 21 | 17.46% | 21.31% | 34.02% | 48.8
23 | 0.0032 | 0.0236 | 0.049 | 75.8 | 0.0036 | 0.0262 | 0.0541 | 83.9 | 0.0039 | 0.0289 | 0.0598 | 92.6 | 10.01% | 21.77% | 34.4% | 68.9 | 23 |  |  | 10.16% | 21.93% | 32.62% | 18.7 | 10 | 22 | 9.626% | 21.39% | 34.05% | 56.1
24 | 0.0028 | 0.0202 | 0.0421 | 65.1 | 0.0031 | 0.0224 | 0.0465 | 72 | 0.0034 | 0.0247 | 0.0513 | 79.4 | 10.53% | 22.24% | 34.8% | 58.9 | 24 |  |  | 11.51% | 22.62% | 35.71% | 25.2 | 11 | 23 | 10.01% | 21.77% | 34.4% | 68.9
Totales |  |  |  | 1267.72 |  |  |  | 1395.2 |  |  |  | 1541 |  |  |  | 1136.11 |  |  |  | 9.603% | 20.2% | 36.75% | 30.2 | 12 | 24 | 10.53% | 22.24% | 34.8% | 58.9
Pérdidas | Año 0 | Año 1 | Año 2 | Año 3
Diaria (kWh) | 1136.11 | 1267.72 | 1395.2 | 1541
Anual (MWh) | 414.6802 | 462.7178 | 509.248 | 562.465
Incremento | 0% | 11.58% | 22.81% | 35.64%
Incremento Anual
PERDIDAS AÑO 3 CON DISP AL 25%
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
TRAFO | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
| 0.0026 |  | 0.0021 | 0.0345 | 0.0016 | 0.0272 | 0.0014 | 0.0229 | 0.0013 | 0.0208 | 0.0011 | 0.0183 | 0.001 | 0.0163 | 0.0009 | 0.0149 | 0.0011 | 0.018 | 0.0013 | 0.0224 | 0.0018 | 0.0293 | 0.0021 | 0.0349 | 0.0024 |  | 0.0034 | 0.0562 | 0.0052 | 0.086 | 0.0061 | 0.1015 | 0.0052 | 0.0867 | 0.0048 | 0.0805 | 0.0035 | 0.0587 | 0.0034 | 0.0567 | 0.0029 |  | 0.0029 | 0.0482 | 0.0036 | 0.0592 | 0.003 | 0.0503
| 0.0026 |  | 0.0021 |  | 0.0016 |  | 0.0014 |  | 0.0013 |  | 0.0011 |  | 0.001 |  | 0.0009 |  | 0.0011 |  | 0.0013 |  | 0.0018 |  | 0.0021 |  | 0.0024 |  | 0.0034 |  | 0.0052 |  | 0.0061 |  | 0.0052 |  | 0.0048 |  | 0.0035 |  | 0.0034 |  | 0.0029 |  | 0.0029 |  | 0.0036 |  | 0.003
LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 25 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 25 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 25 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 25 %
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
| MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
EMPAL-CRAL.ACABOSE_1 |  |  | 0.0118 | 0.0099 | 0.0089 | 0.0074 | 0.0072 | 0.006 | 0.0064 | 0.0053 | 0.0055 | 0.0046 | 0.0052 | 0.0043 | 0.0057 | 0.0047 | 0.0075 | 0.0062 | 0.01 | 0.0084 | 0.0124 | 0.0104 | 0.0167 | 0.014 |  |  | 0.0288 | 0.0241 | 0.0427 | 0.0357 | 0.0521 | 0.0436 | 0.0423 | 0.0354 | 0.0394 | 0.033 | 0.0365 | 0.0306 | 0.0267 | 0.0224 |  |  | 0.0219 | 0.0183 | 0.0255 | 0.0213 | 0.0217 | 0.0181
CRAL ACABOSE_1-CRAL.ACABOSE_2 |  |  | 0.0004 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0006 | 0.0005 |  |  | 0.0011 | 0.0009 | 0.0016 | 0.0014 | 0.002 | 0.0017 | 0.0016 | 0.0014 | 0.0015 | 0.0013 | 0.0014 | 0.0012 | 0.001 | 0.0009 |  |  | 0.0008 | 0.0007 | 0.001 | 0.0008 | 0.0008 | 0.0007
CRAL ACABOSE_2-E.SIRIO_4 |  |  | 0.0004 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0004 | 0.0003 | 0.0005 | 0.0004 |  |  | 0.0009 | 0.0008 | 0.0014 | 0.0011 | 0.0017 | 0.0014 | 0.0014 | 0.0011 | 0.0013 | 0.001 | 0.0012 | 0.001 | 0.0009 | 0.0007 |  |  | 0.0007 | 0.0006 | 0.0008 | 0.0007 | 0.0007 | 0.0006
SUBTOTAL PERDIDAS | 0.0177 |  | 0.0126 |  | 0.0095 |  | 0.0077 |  | 0.0068 |  | 0.0059 |  | 0.0056 |  | 0.0061 |  | 0.008 |  | 0.0107 |  | 0.0133 |  | 0.0178 |  | 0.0207 |  | 0.0308 |  | 0.0457 |  | 0.0558 |  | 0.0453 |  | 0.0422 |  | 0.0391 |  | 0.0286 |  | 0.0238 |  | 0.0234 |  | 0.0273 |  | 0.0232
LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 25% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 25% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 25% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 25%
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
(MW y Mvar) | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
E.SIRIO_1 |  |  | 0.0327 | 0.0273 | 0.0267 | 0.0223 | 0.0232 | 0.0194 | 0.0214 | 0.0178 | 0.0189 | 0.0158 | 0.0163 | 0.0136 | 0.0131 | 0.0109 | 0.0147 | 0.0123 | 0.0172 | 0.0143 | 0.0236 | 0.0197 | 0.025 | 0.0209 |  |  | 0.0376 | 0.0314 | 0.0594 | 0.0496 | 0.0678 | 0.0566 | 0.061 | 0.0509 | 0.0565 | 0.0472 | 0.0318 | 0.0265 | 0.0412 | 0.0344 |  |  | 0.0362 | 0.0303 | 0.0469 | 0.0392 | 0.0398 | 0.0333
E.SIRIO_2 |  |  | 0.0011 | 0.0009 | 0.0009 | 0.0008 | 0.0008 | 0.0007 | 0.0007 | 0.0006 | 0.0007 | 0.0005 | 0.0006 | 0.0005 | 0.0005 | 0.0004 | 0.0005 | 0.0004 | 0.0006 | 0.0005 | 0.0008 | 0.0007 | 0.0009 | 0.0007 |  |  | 0.0013 | 0.0011 | 0.0021 | 0.0017 | 0.0024 | 0.002 | 0.0021 | 0.0018 | 0.002 | 0.0017 | 0.0011 | 0.0009 | 0.0014 | 0.0012 |  |  | 0.0013 | 0.0011 | 0.0016 | 0.0014 | 0.0014 | 0.0012
E.SIRIO_3 |  |  | 0.0016 | 0.0013 | 0.0013 | 0.0011 | 0.0011 | 0.0009 | 0.001 | 0.0009 | 0.0009 | 0.0008 | 0.0008 | 0.0007 | 0.0006 | 0.0005 | 0.0007 | 0.0006 | 0.0008 | 0.0007 | 0.0011 | 0.0009 | 0.0012 | 0.001 |  |  | 0.0016 | 0.0014 | 0.0026 | 0.0022 | 0.0029 | 0.0025 | 0.0026 | 0.0022 | 0.0024 | 0.0021 | 0.001 | 0.0008 | 0.0018 | 0.0015 |  |  | 0.0016 | 0.0013 | 0.002 | 0.0017 | 0.0017 | 0.0014
I.E.S.J.VERNE |  |  | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0005 | 0.0004 | 0.0005 | 0.0004 | 0.0004 | 0.0004 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0005 | 0.0005 |  |  | 0.0006 | 0.0005 | 0.001 | 0.0008 | 0.0011 | 0.0009 | 0.001 | 0.0008 | 0.0009 | 0.0008 | 0.0008 | 0.0006 | 0.0007 | 0.0006 |  |  | 0.0006 | 0.0005 | 0.0008 | 0.0006 | 0.0006 | 0.0005
ESTRELLA.ALTAIR |  |  | 0.0006 | 0.0006 | 0.0005 | 0.0005 | 0.0004 | 0.0005 | 0.0004 | 0.0004 | 0.0003 | 0.0004 | 0.0003 | 0.0003 | 0.0002 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0004 | 0.0004 | 0.0005 | 0.0004 | 0.0005 |  |  | 0.0005 | 0.0006 | 0.0008 | 0.001 | 0.001 | 0.0011 | 0.0009 | 0.001 | 0.0008 | 0.0009 | 0.0007 | 0.0008 | 0.0006 | 0.0007 |  |  | 0.0005 | 0.0006 | 0.0007 | 0.0008 | 0.0006 | 0.0006
AGRICULTORES |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
AGRICULTORES_2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
E.SIRIO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
SUBTOTAL PERDIDAS | 0.0421 |  | 0.0367 |  | 0.03 |  | 0.026 |  | 0.024 |  | 0.0212 |  | 0.0184 |  | 0.0147 |  | 0.0165 |  | 0.0193 |  | 0.0264 |  | 0.028 |  | 0.0304 |  | 0.0416 |  | 0.0659 |  | 0.0752 |  | 0.0676 |  | 0.0626 |  | 0.0354 |  | 0.0457 |  | 0.0387 |  | 0.0402 |  | 0.052 |  | 0.0441
PERDIDAS AÑO 3 CON DISP AL 50% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 50% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 50% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 50% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 50%
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
TRAFO | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
| 0.0026 |  | 0.0024 | 0.0401 | 0.0019 | 0.0322 | 0.0017 | 0.0275 | 0.0015 | 0.0252 | 0.0013 | 0.0224 | 0.0012 | 0.0202 | 0.0011 | 0.0186 | 0.0013 | 0.0221 | 0.0016 | 0.0269 | 0.0021 | 0.0345 | 0.0024 | 0.0405 | 0.0024 |  | 0.003 | 0.0504 | 0.0047 | 0.0787 | 0.0056 | 0.0935 | 0.0048 | 0.0794 | 0.0044 | 0.0735 | 0.0032 | 0.053 | 0.0031 | 0.0509 | 0.0029 |  | 0.0026 | 0.0428 | 0.0032 | 0.0533 | 0.0027 | 0.0449
| 0.0026 |  | 0.0024 |  | 0.0019 |  | 0.0017 |  | 0.0015 |  | 0.0013 |  | 0.0012 |  | 0.0011 |  | 0.0013 |  | 0.0016 |  | 0.0021 |  | 0.0024 |  | 0.0024 |  | 0.003 |  | 0.0047 |  | 0.0056 |  | 0.0048 |  | 0.0044 |  | 0.0032 |  | 0.0031 |  | 0.0029 |  | 0.0026 |  | 0.0032 |  | 0.0027
LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 50 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 50 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 50 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 50 %
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
| MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
EMPAL-CRAL.ACABOSE_1 |  |  | 0.013 | 0.0109 | 0.01 | 0.0083 | 0.0081 | 0.0068 | 0.0073 | 0.0061 | 0.0064 | 0.0053 | 0.006 | 0.005 | 0.0065 | 0.0054 | 0.0084 | 0.0071 | 0.0111 | 0.0093 | 0.0136 | 0.0114 | 0.0182 | 0.0152 |  |  | 0.0272 | 0.0228 | 0.0407 | 0.0341 | 0.0499 | 0.0417 | 0.0403 | 0.0337 | 0.0375 | 0.0314 | 0.0347 | 0.029 | 0.0252 | 0.0211 |  |  | 0.0205 | 0.0172 | 0.0239 | 0.02 | 0.0203 | 0.0169
CRAL ACABOSE_1-CRAL.ACABOSE_2 |  |  | 0.0005 | 0.0004 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0007 | 0.0006 |  |  | 0.0011 | 0.0009 | 0.0016 | 0.0013 | 0.0019 | 0.0016 | 0.0016 | 0.0013 | 0.0015 | 0.0012 | 0.0014 | 0.0011 | 0.001 | 0.0008 |  |  | 0.0008 | 0.0007 | 0.0009 | 0.0008 | 0.0008 | 0.0007
CRAL ACABOSE_2-E.SIRIO_4 |  |  | 0.0004 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0003 | 0.0005 | 0.0004 |  |  | 0.0009 | 0.0007 | 0.0013 | 0.0011 | 0.0016 | 0.0013 | 0.0013 | 0.0011 | 0.0013 | 0.001 | 0.0012 | 0.0009 | 0.0008 | 0.0007 |  |  | 0.0007 | 0.0006 | 0.0008 | 0.0006 | 0.0007 | 0.0005
SUBTOTAL PERDIDAS | 0.0177 |  | 0.0139 |  | 0.0107 |  | 0.0086 |  | 0.0078 |  | 0.0068 |  | 0.0064 |  | 0.0069 |  | 0.0089 |  | 0.0118 |  | 0.0145 |  | 0.0194 |  | 0.0207 |  | 0.0292 |  | 0.0436 |  | 0.0534 |  | 0.0432 |  | 0.0403 |  | 0.0373 |  | 0.027 |  | 0.0238 |  | 0.022 |  | 0.0256 |  | 0.0218
LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 50% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 50% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 50% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 50%
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
(MW y Mvar) | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
E.SIRIO_1 | No se modifica |  | 0.0394 | 0.0329 | 0.0328 | 0.0274 | 0.0289 | 0.0241 | 0.0269 | 0.0224 | 0.0241 | 0.0201 | 0.0211 | 0.0176 | 0.0175 | 0.0146 | 0.0194 | 0.0162 | 0.0222 | 0.0185 | 0.0294 | 0.0246 | 0.031 | 0.0258 |  |  | 0.032 | 0.0267 | 0.0522 | 0.0436 | 0.0601 | 0.0502 | 0.0537 | 0.0449 | 0.0495 | 0.0413 | 0.0272 | 0.0227 | 0.0353 | 0.0295 |  |  | 0.0308 | 0.0257 | 0.0406 | 0.0339 | 0.0341 | 0.0285
E.SIRIO_2 |  |  | 0.0014 | 0.0011 | 0.0011 | 0.0009 | 0.001 | 0.0008 | 0.0009 | 0.0008 | 0.0008 | 0.0007 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0007 | 0.0006 | 0.0008 | 0.0006 | 0.001 | 0.0008 | 0.0011 | 0.0009 |  |  | 0.0011 | 0.0009 | 0.0018 | 0.0015 | 0.0021 | 0.0018 | 0.0019 | 0.0016 | 0.0017 | 0.0015 | 0.0009 | 0.0008 | 0.0012 | 0.001 |  |  | 0.0011 | 0.0009 | 0.0014 | 0.0012 | 0.0012 | 0.001
E.SIRIO_3 |  |  | 0.002 | 0.0016 | 0.0016 | 0.0014 | 0.0015 | 0.0012 | 0.0014 | 0.0011 | 0.0012 | 0.001 | 0.0011 | 0.0009 | 0.0009 | 0.0008 | 0.001 | 0.0008 | 0.0011 | 0.001 | 0.0015 | 0.0012 | 0.0016 | 0.0013 |  |  | 0.0013 | 0.0011 | 0.0022 | 0.0018 | 0.0025 | 0.0021 | 0.0022 | 0.0019 | 0.0021 | 0.0017 | 0.0008 | 0.0007 | 0.0015 | 0.0012 |  |  | 0.0013 | 0.0011 | 0.0017 | 0.0014 | 0.0014 | 0.0012
I.E.S.J.VERNE |  |  | 0.0009 | 0.0008 | 0.0008 | 0.0007 | 0.0007 | 0.0006 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0006 | 0.0005 | 0.0005 | 0.0004 | 0.0005 | 0.0004 | 0.0006 | 0.0005 | 0.0007 | 0.0006 | 0.0008 | 0.0006 |  |  | 0.0004 | 0.0004 | 0.0008 | 0.0006 | 0.0009 | 0.0007 | 0.0008 | 0.0007 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0005 | 0.0004 |  |  | 0.0004 | 0.0003 | 0.0006 | 0.0005 | 0.0005 | 0.0004
ESTRELLA.ALTAIR |  |  | 0.0007 | 0.0009 | 0.0006 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0006 | 0.0005 | 0.0006 | 0.0004 | 0.0005 | 0.0004 | 0.0004 | 0.0004 | 0.0005 | 0.0004 | 0.0005 | 0.0006 | 0.0007 | 0.0006 | 0.0007 |  |  | 0.0004 | 0.0005 | 0.0007 | 0.0008 | 0.0008 | 0.0009 | 0.0007 | 0.0008 | 0.0006 | 0.0007 | 0.0005 | 0.0006 | 0.0004 | 0.0005 |  |  | 0.0004 | 0.0004 | 0.0005 | 0.0006 | 0.0004 | 0.0005
AGRICULTORES |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
AGRICULTORES_2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
E.SIRIO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
SUBTOTAL PERDIDAS | 0.0421 |  | 0.0444 |  | 0.0369 |  | 0.0327 |  | 0.0304 |  | 0.0272 |  | 0.0239 |  | 0.0199 |  | 0.022 |  | 0.0251 |  | 0.0332 |  | 0.0351 |  | 0.0304 |  | 0.0352 |  | 0.0577 |  | 0.0664 |  | 0.0593 |  | 0.0546 |  | 0.03 |  | 0.0389 |  | 0.0387 |  | 0.034 |  | 0.0448 |  | 0.0376
PERDIDAS AÑO 3 CON DISP AL 75% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 75% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 75% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 75% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 75%
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
TRAFO | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
| 0.0026 |  | 0.0021 | 0.0345 | 0.0023 | 0.0376 | 0.002 | 0.0326 | 0.0018 | 0.03 | 0.0016 | 0.027 | 0.0015 | 0.0246 | 0.0014 | 0.0228 | 0.0016 | 0.0266 | 0.0019 | 0.0319 | 0.0024 | 0.0401 | 0.0028 | 0.0465 | 0.0024 |  | 0.0027 | 0.0452 | 0.0043 | 0.072 | 0.0052 | 0.0862 | 0.0044 | 0.0727 | 0.004 | 0.0671 | 0.0029 | 0.0478 | 0.0027 | 0.0456 | 0.0029 |  | 0.0023 | 0.0381 | 0.0029 | 0.0479 | 0.0024 | 0.04
| 0.0026 |  | 0.0021 |  | 0.0023 |  | 0.002 |  | 0.0018 |  | 0.0016 |  | 0.0015 |  | 0.0014 |  | 0.0016 |  | 0.0019 |  | 0.0024 |  | 0.0028 |  | 0.0024 |  | 0.0027 |  | 0.0043 |  | 0.0052 |  | 0.0044 |  | 0.004 |  | 0.0029 |  | 0.0027 |  | 0.0029 |  | 0.0023 |  | 0.0029 |  | 0.0024
LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 75 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 75 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 75 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 75 %
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
| MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
EMPAL-CRAL.ACABOSE_1 | No se modifica |  | 0.0118 | 0.0099 | 0.0111 | 0.0093 | 0.0092 | 0.0077 | 0.0082 | 0.0069 | 0.0073 | 0.0061 | 0.0069 | 0.0058 | 0.0074 | 0.0062 | 0.0095 | 0.0079 | 0.0123 | 0.0103 | 0.0149 | 0.0125 | 0.0197 | 0.0165 |  |  | 0.0257 | 0.0215 | 0.0388 | 0.0325 | 0.0478 | 0.04 | 0.0384 | 0.0322 | 0.0357 | 0.0298 | 0.0329 | 0.0276 | 0.0237 | 0.0198 |  |  | 0.0192 | 0.016 | 0.0225 | 0.0188 | 0.0189 | 0.0158
CRAL ACABOSE_1-CRAL.ACABOSE_2 |  |  | 0.0004 | 0.0004 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0004 | 0.0005 | 0.0005 | 0.0007 | 0.0006 |  |  | 0.001 | 0.0008 | 0.0015 | 0.0013 | 0.0019 | 0.0016 | 0.0015 | 0.0013 | 0.0014 | 0.0012 | 0.0013 | 0.0011 | 0.0009 | 0.0008 |  |  | 0.0008 | 0.0006 | 0.0009 | 0.0007 | 0.0007 | 0.0006
CRAL ACABOSE_2-E.SIRIO_4 |  |  | 0.0004 | 0.0003 | 0.0003 | 0.0002 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0001 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0003 | 0.0003 | 0.0004 | 0.0003 | 0.0006 | 0.0005 |  |  | 0.0009 | 0.0007 | 0.0013 | 0.001 | 0.0016 | 0.0013 | 0.0013 | 0.001 | 0.0012 | 0.001 | 0.0011 | 0.0009 | 0.0008 | 0.0006 |  |  | 0.0007 | 0.0005 | 0.0008 | 0.0006 | 0.0007 | 0.0005
SUBTOTAL PERDIDAS | 0.0177 |  | 0.0126 |  | 0.0118 |  | 0.0098 |  | 0.0087 |  | 0.0078 |  | 0.0073 |  | 0.0079 |  | 0.0101 |  | 0.013 |  | 0.0158 |  | 0.021 |  | 0.0207 |  | 0.0276 |  | 0.0416 |  | 0.0513 |  | 0.0412 |  | 0.0383 |  | 0.0353 |  | 0.0254 |  | 0.0238 |  | 0.0207 |  | 0.0242 |  | 0.0203
LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 75% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 75% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 75% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 75%
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
(MW y Mvar) | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
E.SIRIO_1 | No se modifica |  | 0.0327 | 0.0273 | 0.0395 | 0.033 | 0.0352 | 0.0294 | 0.033 | 0.0276 | 0.0299 | 0.025 | 0.0266 | 0.0222 | 0.0225 | 0.0188 | 0.0247 | 0.0206 | 0.0278 | 0.0232 | 0.0358 | 0.0299 | 0.0375 | 0.0313 |  |  | 0.0271 | 0.0227 | 0.0458 | 0.0383 | 0.0532 | 0.0444 | 0.0472 | 0.0394 | 0.0433 | 0.0362 | 0.0232 | 0.0194 | 0.0302 | 0.0252 |  |  | 0.026 | 0.0217 | 0.0351 | 0.0293 | 0.0291 | 0.0243
E.SIRIO_2 |  |  | 0.0011 | 0.0009 | 0.0014 | 0.0011 | 0.0012 | 0.001 | 0.0011 | 0.0009 | 0.001 | 0.0009 | 0.0009 | 0.0008 | 0.0008 | 0.0006 | 0.0008 | 0.0007 | 0.001 | 0.0008 | 0.0012 | 0.001 | 0.0013 | 0.0011 |  |  | 0.001 | 0.0008 | 0.0016 | 0.0014 | 0.0019 | 0.0016 | 0.0017 | 0.0014 | 0.0015 | 0.0013 | 0.0008 | 0.0007 | 0.0011 | 0.0009 |  |  | 0.0009 | 0.0008 | 0.0012 | 0.001 | 0.001 | 0.0009
E.SIRIO_3 |  |  | 0.0016 | 0.0013 | 0.0021 | 0.0017 | 0.0019 | 0.0016 | 0.0017 | 0.0015 | 0.0016 | 0.0013 | 0.0014 | 0.0012 | 0.0012 | 0.001 | 0.0013 | 0.0011 | 0.0015 | 0.0013 | 0.0019 | 0.0016 | 0.002 | 0.0016 |  |  | 0.0011 | 0.0009 | 0.0018 | 0.0015 | 0.0021 | 0.0018 | 0.0019 | 0.0016 | 0.0017 | 0.0014 | 0.0007 | 0.0006 | 0.0012 | 0.001 |  |  | 0.001 | 0.0008 | 0.0014 | 0.0012 | 0.0011 | 0.0009
I.E.S.J.VERNE |  |  | 0.0007 | 0.0006 | 0.0011 | 0.0009 | 0.001 | 0.0008 | 0.0009 | 0.0008 | 0.0009 | 0.0007 | 0.0008 | 0.0007 | 0.0007 | 0.0006 | 0.0007 | 0.0006 | 0.0008 | 0.0007 | 0.001 | 0.0008 | 0.001 | 0.0009 |  |  | 0.0003 | 0.0003 | 0.0006 | 0.0005 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0005 | 0.0005 | 0.0004 | 0.0004 | 0.0004 | 0.0003 |  |  | 0.0003 | 0.0003 | 0.0004 | 0.0004 | 0.0003 | 0.0003
ESTRELLA.ALTAIR |  |  | 0.0006 | 0.0006 | 0.0008 | 0.001 | 0.0007 | 0.0009 | 0.0007 | 0.0008 | 0.0007 | 0.0008 | 0.0006 | 0.0007 | 0.0005 | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.0007 | 0.0008 | 0.0009 | 0.0008 | 0.0009 |  |  | 0.0003 | 0.0003 | 0.0005 | 0.0006 | 0.0006 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 0.0006 | 0.0004 | 0.0005 | 0.0003 | 0.0004 |  |  | 0.0003 | 0.0003 | 0.0004 | 0.0005 | 0.0003 | 0.0004
AGRICULTORES |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
AGRICULTORES_2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
E.SIRIO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
SUBTOTAL PERDIDAS | 0.0421 |  | 0.0367 |  | 0.0449 |  | 0.04 |  | 0.0374 |  | 0.0341 |  | 0.0303 |  | 0.0257 |  | 0.0281 |  | 0.0317 |  | 0.0407 |  | 0.0426 |  | 0.0304 |  | 0.0298 |  | 0.0503 |  | 0.0585 |  | 0.052 |  | 0.0475 |  | 0.0255 |  | 0.0332 |  | 0.0387 |  | 0.0285 |  | 0.0385 |  | 0.0318
PERDIDAS AÑO 3 CON DISP AL 100% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 100% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 100% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 100% | [8 empty] | PERDIDAS AÑO 3 CON DISP AL 100%
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
TRAFO | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS
| 0.0026 |  | 0.0032 | 0.0527 | 0.0026 | 0.0436 | 0.0023 | 0.0382 | 0.0021 | 0.0355 | 0.0019 | 0.0322 | 0.0018 | 0.0295 | 0.0017 | 0.0276 | 0.0019 | 0.0318 | 0.0023 | 0.0374 | 0.0028 | 0.0463 | 0.0032 | 0.0531 | 0.0024 |  | 0.0024 | 0.0404 | 0.004 | 0.0658 | 0.0048 | 0.0793 | 0.004 | 0.0664 | 0.0037 | 0.061 | 0.0025 | 0.0409 | 0.0023 | 0.0385 | 0.0029 |  | 0.0019 | 0.0317 | 0.0026 | 0.0429 | 0.0021 | 0.0355
| 0.0026 |  | 0.0032 |  | 0.0026 |  | 0.0023 |  | 0.0021 |  | 0.0019 |  | 0.0018 |  | 0.0017 |  | 0.0019 |  | 0.0023 |  | 0.0028 |  | 0.0032 |  | 0.0024 |  | 0.0024 |  | 0.004 |  | 0.0048 |  | 0.004 |  | 0.0037 |  | 0.0025 |  | 0.0023 |  | 0.0029 |  | 0.0019 |  | 0.0026 |  | 0.0021
LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 100 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 100 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 100 % | [11 empty] | LINEA EMPALME-CORRAL DEL ACABOSE AÑO 3 CON DISP AL 100 %
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24 |  | Line Records |  |  |  | Line Records
| MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | From Number | From Name | To Number | To Name | % of MVA Limit (Max) | MW Loss | Mvar Loss
EMPAL-CRAL.ACABOSE_1 | No se modifica |  | 0.0157 | 0.0131 | 0.0123 | 0.0103 | 0.0103 | 0.0086 | 0.0093 | 0.0078 | 0.0083 | 0.0069 | 0.0079 | 0.0066 | 0.0084 | 0.0071 | 0.0106 | 0.0089 | 0.0136 | 0.0114 | 0.0163 | 0.0137 | 0.0213 | 0.0178 | No se Modifica |  | 0.0242 | 0.0202 | 0.037 | 0.0309 | 0.0457 | 0.0382 | 0.0366 | 0.0306 | 0.0339 | 0.0284 | 0.0305 | 0.0255 | 0.0216 | 0.0181 |  |  | 0.0173 | 0.0145 | 0.0211 | 0.0177 | 0.0177 | 0.0148 | 13 | Nudo Slack. | 1 | Empalme.
CRAL ACABOSE_1-CRAL.ACABOSE_2 |  |  | 0.0006 | 0.0005 | 0.0004 | 0.0004 | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0003 | 0.0002 | 0.0003 | 0.0002 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0006 | 0.0005 | 0.0008 | 0.0006 |  |  | 0.001 | 0.0008 | 0.0015 | 0.0012 | 0.0018 | 0.0015 | 0.0014 | 0.0012 | 0.0013 | 0.0011 | 0.0012 | 0.001 | 0.0009 | 0.0007 |  |  | 0.0007 | 0.0006 | 0.0008 | 0.0007 | 0.0007 | 0.0006 | 1 | Empalme. | 2 | CRAL.ACABOSE_1
CRAL ACABOSE_2-E.SIRIO_4 |  |  | 0.0004 | 0.0003 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0002 | 0.0003 | 0.0002 | 0.0004 | 0.0003 | 0.0005 | 0.0004 | 0.0006 | 0.0005 |  |  | 0.0008 | 0.0007 | 0.0013 | 0.001 | 0.0016 | 0.0013 | 0.0013 | 0.001 | 0.0012 | 0.0009 | 0.0011 | 0.0009 | 0.0008 | 0.0006 |  |  | 0.0006 | 0.0005 | 0.0007 | 0.0006 | 0.0006 | 0.0005 | 2 | CRAL.ACABOSE_1 | 3 | CRAL.ACABOSE_2
SUBTOTAL PERDIDAS | [48 empty] | 3 | CRAL.ACABOSE_2 | 4 | E.SIRIO_4
| 0.0177 |  | 0.0167 |  | 0.013 |  | 0.011 |  | 0.0098 |  | 0.0088 |  | 0.0084 |  | 0.0089 |  | 0.0113 |  | 0.0145 |  | 0.0174 |  | 0.0227 |  | 0.0207 |  | 0.026 |  | 0.0398 |  | 0.0491 |  | 0.0393 |  | 0.0364 |  | 0.0328 |  | 0.0233 |  | 0.0238 |  | 0.0186 |  | 0.0226 |  | 0.019 |  | 1 | Empalme. | 5 | E.SIRIO_1
LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 100% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 100% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 100% | [11 empty] | LINEA EMPALME ESTRELLA SIRIO. AÑO 3 CON DISP AL 100% | [12 empty] | 5 | E.SIRIO_1 | 6 | E.SIRIO_2
Hora | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24 |  | 6 | E.SIRIO_2 | 7 | E.SIRIO_3
(MW y Mvar) | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | MW LOSS | Mvar LOSS | 7 | E.SIRIO_3 | 8 | I.E.S.J.VERNE
E.SIRIO_1 | No se modifica |  | 0.055 | 0.0459 | 0.0471 | 0.0394 | 0.0424 | 0.0354 | 0.04 | 0.0334 | 0.0366 | 0.0306 | 0.033 | 0.0275 | 0.0284 | 0.0237 | 0.0308 | 0.0257 | 0.0342 | 0.0286 | 0.0431 | 0.036 | 0.0449 | 0.0375 | No se Modifica |  | 0.0229 | 0.0191 | 0.0401 | 0.0335 | 0.0469 | 0.0391 | 0.0414 | 0.0345 | 0.0377 | 0.0315 | 0.0185 | 0.0154 | 0.0237 | 0.0198 |  |  | 0.0201 | 0.0168 | 0.0301 | 0.0252 | 0.0246 | 0.0206 | 8 | I.E.S.J.VERNE | 9 | E.ALTAIR
E.SIRIO_2 |  |  | 0.0019 | 0.0016 | 0.0016 | 0.0013 | 0.0015 | 0.0012 | 0.0014 | 0.0011 | 0.0013 | 0.001 | 0.0011 | 0.0009 | 0.001 | 0.0008 | 0.0011 | 0.0009 | 0.0012 | 0.001 | 0.0015 | 0.0012 | 0.0015 | 0.0013 |  |  | 0.0008 | 0.0007 | 0.0014 | 0.0012 | 0.0017 | 0.0014 | 0.0015 | 0.0012 | 0.0013 | 0.0011 | 0.0006 | 0.0005 | 0.0008 | 0.0007 |  |  | 0.0007 | 0.0006 | 0.0011 | 0.0009 | 0.0009 | 0.0007 | 9 | E.ALTAIR | 10 | AGRICULTORES
E.SIRIO_3 |  |  | 0.0029 | 0.0025 | 0.0025 | 0.0021 | 0.0023 | 0.0019 | 0.0022 | 0.0018 | 0.002 | 0.0017 | 0.0018 | 0.0015 | 0.0016 | 0.0014 | 0.0017 | 0.0015 | 0.0019 | 0.0016 | 0.0023 | 0.002 | 0.0024 | 0.002 |  |  | 0.0008 | 0.0007 | 0.0015 | 0.0013 | 0.0018 | 0.0015 | 0.0016 | 0.0013 | 0.0014 | 0.0012 | 0.0006 | 0.0005 | 0.0009 | 0.0007 |  |  | 0.0007 | 0.0006 | 0.0011 | 0.0009 | 0.0009 | 0.0008 | 10 | AGRICULTORES | 14 | AGRICULTORES_2
I.E.S.J.VERNE |  |  | 0.0016 | 0.0013 | 0.0014 | 0.0012 | 0.0013 | 0.0011 | 0.0012 | 0.001 | 0.0012 | 0.001 | 0.0011 | 0.0009 | 0.001 | 0.0008 | 0.001 | 0.0009 | 0.0011 | 0.0009 | 0.0013 | 0.0011 | 0.0014 | 0.0011 |  |  | 0.0002 | 0.0002 | 0.0004 | 0.0004 | 0.0005 | 0.0005 | 0.0005 | 0.0004 | 0.0004 | 0.0004 | 0.0003 | 0.0002 | 0.0002 | 0.0002 |  |  | 0.0002 | 0.0002 | 0.0003 | 0.0003 | 0.0003 | 0.0002 | 14 | AGRICULTORES_2 | 15 | E.SIRIO
ESTRELLA.ALTAIR |  |  | 0.0012 | 0.0014 | 0.0011 | 0.0012 | 0.001 | 0.0011 | 0.0009 | 0.0011 | 0.0009 | 0.001 | 0.0008 | 0.0009 | 0.0007 | 0.0008 | 0.0008 | 0.0009 | 0.0008 | 0.0009 | 0.001 | 0.0011 | 0.001 | 0.0012 |  |  | 0.0002 | 0.0003 | 0.0004 | 0.0005 | 0.0005 | 0.0006 | 0.0004 | 0.0005 | 0.0004 | 0.0005 | 0.0003 | 0.0003 | 0.0002 | 0.0003 |  |  | 0.0002 | 0.0002 | 0.0003 | 0.0004 | 0.0002 | 0.0003
AGRICULTORES |  |  | 0.0001 | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0001 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
AGRICULTORES_2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
E.SIRIO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
SUBTOTAL PERDIDAS | 0.0421 |  | 0.0627 |  | 0.0538 |  | 0.0485 |  | 0.0457 |  | 0.042 |  | 0.0378 |  | 0.0327 |  | 0.0354 |  | 0.0392 |  | 0.0492 |  | 0.0513 |  | 0.0304 |  | 0.0249 |  | 0.0438 |  | 0.0514 |  | 0.0454 |  | 0.0412 |  | 0.0203 |  | 0.0258 |  | 0.0387 |  | 0.0219 |  | 0.0329 |  | 0.0269
| AÑO 3 (MWh) |  |  |  | AÑO 3 25% (MWh) |  |  |  | AÑO 3 50% (MWh) |  |  |  | AÑO 3 75% (MWh) |  |  |  | AÑO 3 100% (MWh)
Hora | TRAFO | E-C | E-ES | Total (kWh) | TRAFO | E-C | E-ES | Total (kWh) | TRAFO | E-C | E-ES | Total (kWh) | TRAFO | E-C | E-ES | Total (kWh) | TRAFO | E-C | E-ES | Total (kWh)
1 | 0.0026 | 0.0177 | 0.0421 | 62.4 | 0.0026 | 0.0177 | 0.0421 | 62.4 | 0.0026 | 0.0177 | 0.0421 | 62.4 | 0.0026 | 0.0177 | 0.0421 | 62.4 | 0.0026 | 0.0177 | 0.0421 | 62.4
2 | 0.0018 | 0.0114 | 0.0297 | 42.9 | 0.0021 | 0.0126 | 0.0367 | 51.4 | 0.0024 | 0.0139 | 0.0444 | 60.7 | 0.0021 | 0.0126 | 0.0367 | 51.4 | 0.0032 | 0.0167 | 0.0627 | 82.6
3 | 0.0014 | 0.0085 | 0.0238 | 33.7 | 0.0016 | 0.0095 | 0.03 | 41.1 | 0.0019 | 0.0107 | 0.0369 | 49.5 | 0.0023 | 0.0118 | 0.0449 | 59 | 0.0026 | 0.013 | 0.0538 | 69.4
4 | 0.0011 | 0.0067 | 0.0202 | 28 | 0.0014 | 0.0077 | 0.026 | 35.1 | 0.0017 | 0.0086 | 0.0327 | 43 | 0.002 | 0.0098 | 0.04 | 51.8 | 0.0023 | 0.011 | 0.0485 | 61.8
5 | 0.001 | 0.0059 | 0.0185 | 25.4 | 0.0013 | 0.0068 | 0.024 | 32.1 | 0.0015 | 0.0078 | 0.0304 | 39.7 | 0.0018 | 0.0087 | 0.0374 | 47.9 | 0.0021 | 0.0098 | 0.0457 | 57.6
6 | 0.0009 | 0.0052 | 0.016 | 22.1 | 0.0011 | 0.0059 | 0.0212 | 28.2 | 0.0013 | 0.0068 | 0.0272 | 35.3 | 0.0016 | 0.0078 | 0.0341 | 43.5 | 0.0019 | 0.0088 | 0.042 | 52.7
7 | 0.0008 | 0.0047 | 0.0136 | 19.1 | 0.001 | 0.0056 | 0.0184 | 25 | 0.0012 | 0.0064 | 0.0239 | 31.5 | 0.0015 | 0.0073 | 0.0303 | 39.1 | 0.0018 | 0.0084 | 0.0378 | 48
8 | 0.0007 | 0.0053 | 0.0104 | 16.4 | 0.0009 | 0.0061 | 0.0147 | 21.7 | 0.0011 | 0.0069 | 0.0199 | 27.9 | 0.0014 | 0.0079 | 0.0257 | 35 | 0.0017 | 0.0089 | 0.0327 | 43.3
9 | 0.0009 | 0.0071 | 0.0121 | 20.1 | 0.0011 | 0.008 | 0.0165 | 25.6 | 0.0013 | 0.0089 | 0.022 | 32.2 | 0.0016 | 0.0101 | 0.0281 | 39.8 | 0.0019 | 0.0113 | 0.0354 | 48.6
10 | 0.0011 | 0.0092 | 0.0145 | 24.8 | 0.0013 | 0.0107 | 0.0193 | 31.3 | 0.0016 | 0.0118 | 0.0251 | 38.5 | 0.0019 | 0.013 | 0.0317 | 46.6 | 0.0023 | 0.0145 | 0.0392 | 56
11 | 0.0015 | 0.012 | 0.0207 | 34.2 | 0.0018 | 0.0133 | 0.0264 | 41.5 | 0.0021 | 0.0145 | 0.0332 | 49.8 | 0.0024 | 0.0158 | 0.0407 | 58.9 | 0.0028 | 0.0174 | 0.0492 | 69.4
12 | 0.0018 | 0.0167 | 0.0228 | 41.3 | 0.0021 | 0.0178 | 0.028 | 47.9 | 0.0024 | 0.0194 | 0.0351 | 56.9 | 0.0028 | 0.021 | 0.0426 | 66.4 | 0.0032 | 0.0227 | 0.0513 | 77.2
13 | 0.0024 | 0.0207 | 0.0304 | 53.5 | 0.0024 | 0.0207 | 0.0304 | 53.5 | 0.0024 | 0.0207 | 0.0304 | 53.5 | 0.0024 | 0.0207 | 0.0304 | 53.5 | 0.0024 | 0.0207 | 0.0304 | 53.5
14 | 0.0037 | 0.0327 | 0.0486 | 85 | 0.0034 | 0.0308 | 0.0416 | 75.8 | 0.003 | 0.0292 | 0.0352 | 67.4 | 0.0027 | 0.0276 | 0.0298 | 60.1 | 0.0024 | 0.026 | 0.0249 | 53.3
15 | 0.0056 | 0.0478 | 0.0745 | 127.9 | 0.0052 | 0.0457 | 0.0659 | 116.8 | 0.0047 | 0.0436 | 0.0577 | 106 | 0.0043 | 0.0416 | 0.0503 | 96.2 | 0.004 | 0.0398 | 0.0438 | 87.6
16 | 0.0066 | 0.0582 | 0.0846 | 149.4 | 0.0061 | 0.0558 | 0.0752 | 137.1 | 0.0056 | 0.0534 | 0.0664 | 125.4 | 0.0052 | 0.0513 | 0.0585 | 115 | 0.0048 | 0.0491 | 0.0514 | 105.3
17 | 0.0057 | 0.0475 | 0.0765 | 129.7 | 0.0052 | 0.0453 | 0.0676 | 118.1 | 0.0048 | 0.0432 | 0.0593 | 107.3 | 0.0044 | 0.0412 | 0.052 | 97.6 | 0.004 | 0.0393 | 0.0454 | 88.7
18 | 0.0052 | 0.0424 | 0.0712 | 118.8 | 0.0048 | 0.0422 | 0.0626 | 109.6 | 0.0044 | 0.0403 | 0.0546 | 99.3 | 0.004 | 0.0383 | 0.0475 | 89.8 | 0.0037 | 0.0364 | 0.0412 | 81.3
19 | 0.0047 | 0.0412 | 0.0607 | 106.6 | 0.0035 | 0.0391 | 0.0354 | 78 | 0.0032 | 0.0373 | 0.03 | 70.5 | 0.0029 | 0.0353 | 0.0255 | 63.7 | 0.0025 | 0.0328 | 0.0203 | 55.6
20 | 0.0038 | 0.0303 | 0.053 | 87.1 | 0.0034 | 0.0286 | 0.0457 | 77.7 | 0.0031 | 0.027 | 0.0389 | 69 | 0.0027 | 0.0254 | 0.0332 | 61.3 | 0.0023 | 0.0233 | 0.0258 | 51.4
21 | 0.0029 | 0.0238 | 0.0387 | 65.4 | 0.0029 | 0.0238 | 0.0387 | 65.4 | 0.0029 | 0.0238 | 0.0387 | 65.4 | 0.0029 | 0.0238 | 0.0387 | 65.4 | 0.0029 | 0.0238 | 0.0387 | 65.4
22 | 0.0032 | 0.025 | 0.047 | 75.2 | 0.0029 | 0.0234 | 0.0402 | 66.5 | 0.0026 | 0.022 | 0.034 | 58.6 | 0.0023 | 0.0207 | 0.0285 | 51.5 | 0.0019 | 0.0186 | 0.0219 | 42.4
23 | 0.0039 | 0.0289 | 0.0598 | 92.6 | 0.0036 | 0.0273 | 0.052 | 82.9 | 0.0032 | 0.0256 | 0.0448 | 73.6 | 0.0029 | 0.0242 | 0.0385 | 65.6 | 0.0026 | 0.0226 | 0.0329 | 58.1
24 | 0.0034 | 0.0247 | 0.0513 | 79.4 | 0.003 | 0.0232 | 0.0441 | 70.3 | 0.0027 | 0.0218 | 0.0376 | 62.1 | 0.0024 | 0.0203 | 0.0318 | 54.5 | 0.0021 | 0.019 | 0.0269 | 48
| 0.0667 | 0.5336 | 0.9407 | 1541 | 0.0647 | 0.5276 | 0.9027 | 1495 | 0.0637 | 0.5213 | 0.9005 | 1485.5 | 0.0631 | 0.5139 | 0.899 | 1476 | 0.064 | 0.5116 | 0.944 | 1519.6
[5 empty] | 0.97015 | [5 empty] | 0.99365 |  |  |  | 0.9936
| Pérdidas diarias |  |  |  | Pérdidas anuales
| Periodo | kWh |  |  | Periodo | kWh | %
| año 3 | 1541 |  |  | año 3 | 562465 | 0
| 25% | 1495 |  |  | 25% | 545675 | 2.9851
| 50% | 1485.5 |  |  | 50% | 542207.5 | 3.6016
| 75% | 1476 |  |  | 75% | 538740 | 4.218
| 100% | 1519.6 |  |  | 100% | 554654 | 1.3887

## TENSION
AÑO 1
HORA |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
NUDO |  | PU | KV | PU | KV | PU | KV | PU | KV | PU | KV | PU | KV | PU | KV | PU | KV | PU | KV | PU | KV | PU | KV | PU | KV
Empalme. |  | 0.99685 | 14.953 | 0.9974 | 14.961 | 0.99772 | 14.966 | 0.99792 | 14.969 | 0.99803 | 14.97 | 0.99817 | 14.972 | 0.99828 | 14.974 | 0.99836 | 14.975 | 0.99818 | 14.973 | 0.99795 | 14.969 | 0.99762 | 14.964 | 0.99739 | 14.961 | 0.99701 | 14.955 | 0.99623 | 14.943 | 0.99539 | 14.931 | 0.99501 | 14.925 | 0.99537 | 14.931 | 0.99554 | 14.933 | 0.99578 | 14.937 | 0.99622 | 14.943 | 0.99622 | 14.943 | 0.99649 | 14.947 | 0.99614 | 14.942 | 0.99642 | 14.946
CRAL.ACABOSE_1 |  | 0.99026 | 14.854 | 0.99211 | 14.882 | 0.99317 | 14.897 | 0.99385 | 14.908 | 0.99422 | 14.913 | 0.99463 | 14.919 | 0.99486 | 14.923 | 0.99479 | 14.922 | 0.99403 | 14.91 | 0.9931 | 14.897 | 0.9922 | 14.883 | 0.99104 | 14.866 | 0.98987 | 14.848 | 0.98729 | 14.809 | 0.98457 | 14.769 | 0.98308 | 14.746 | 0.98459 | 14.769 | 0.98516 | 14.777 | 0.98574 | 14.786 | 0.9876 | 14.814 | 0.9876 | 14.814 | 0.98867 | 14.83 | 0.98772 | 14.816 | 0.98864 | 14.83
CRAL.ACABOSE_2 |  | 0.98994 | 14.849 | 0.99185 | 14.878 | 0.99295 | 14.894 | 0.99365 | 14.905 | 0.99403 | 14.911 | 0.99446 | 14.917 | 0.99469 | 14.92 | 0.99461 | 14.919 | 0.99383 | 14.907 | 0.99287 | 14.893 | 0.99193 | 14.879 | 0.99073 | 14.861 | 0.98953 | 14.843 | 0.98686 | 14.803 | 0.98404 | 14.761 | 0.98251 | 14.738 | 0.98407 | 14.761 | 0.98466 | 14.77 | 0.98525 | 14.779 | 0.98718 | 14.808 | 0.98718 | 14.808 | 0.98829 | 14.824 | 0.98732 | 14.81 | 0.98826 | 14.824
E.SIRIO_4 |  | 0.98957 | 14.844 | 0.99156 | 14.873 | 0.99269 | 14.89 | 0.99342 | 14.901 | 0.99382 | 14.907 | 0.99426 | 14.914 | 0.9945 | 14.918 | 0.99441 | 14.916 | 0.99359 | 14.904 | 0.99259 | 14.889 | 0.99163 | 14.874 | 0.99037 | 14.856 | 0.98913 | 14.837 | 0.98636 | 14.795 | 0.98344 | 14.752 | 0.98184 | 14.728 | 0.98347 | 14.752 | 0.98407 | 14.761 | 0.98469 | 14.77 | 0.9867 | 14.8 | 0.9867 | 14.8 | 0.98785 | 14.818 | 0.98684 | 14.803 | 0.98782 | 14.817
E.SIRIO_1 |  | 0.98498 | 14.775 | 0.9873 | 14.809 | 0.9888 | 14.832 | 0.98965 | 14.845 | 0.99016 | 14.852 | 0.99082 | 14.862 | 0.99153 | 14.873 | 0.99243 | 14.886 | 0.99192 | 14.879 | 0.99099 | 14.865 | 0.98929 | 14.839 | 0.98879 | 14.832 | 0.98703 | 14.805 | 0.98349 | 14.752 | 0.97961 | 14.694 | 0.97822 | 14.673 | 0.97939 | 14.691 | 0.98013 | 14.702 | 0.98153 | 14.723 | 0.98291 | 14.744 | 0.98291 | 14.744 | 0.98398 | 14.76 | 0.98201 | 14.73 | 0.98332 | 14.75
E.SIRIO_2 |  | 0.98452 | 14.768 | 0.98691 | 14.804 | 0.98845 | 14.827 | 0.98933 | 14.84 | 0.98985 | 14.848 | 0.99054 | 14.858 | 0.99126 | 14.869 | 0.9922 | 14.883 | 0.99168 | 14.875 | 0.99072 | 14.861 | 0.98897 | 14.834 | 0.98845 | 14.827 | 0.98664 | 14.8 | 0.983 | 14.745 | 0.979 | 14.685 | 0.97757 | 14.664 | 0.97877 | 14.682 | 0.97953 | 14.693 | 0.98098 | 14.715 | 0.9824 | 14.736 | 0.9824 | 14.736 | 0.98349 | 14.752 | 0.98146 | 14.722 | 0.98281 | 14.742
E.SIRIO_3 |  | 0.98361 | 14.754 | 0.98614 | 14.792 | 0.98777 | 14.816 | 0.98869 | 14.83 | 0.98924 | 14.839 | 0.98997 | 14.85 | 0.99074 | 14.861 | 0.99174 | 14.876 | 0.99118 | 14.868 | 0.99019 | 14.853 | 0.98832 | 14.825 | 0.98779 | 14.817 | 0.98587 | 14.788 | 0.98201 | 14.73 | 0.97778 | 14.667 | 0.97627 | 14.644 | 0.97754 | 14.663 | 0.97834 | 14.675 | 0.97988 | 14.698 | 0.98137 | 14.721 | 0.98137 | 14.721 | 0.98252 | 14.738 | 0.98037 | 14.705 | 0.9818 | 14.727
I.E.S.J.VERNE |  | 0.98297 | 14.745 | 0.98561 | 14.784 | 0.98729 | 14.809 | 0.98825 | 14.824 | 0.98882 | 14.832 | 0.98958 | 14.844 | 0.99038 | 14.856 | 0.99142 | 14.871 | 0.99084 | 14.863 | 0.98982 | 14.847 | 0.98788 | 14.818 | 0.98733 | 14.81 | 0.98533 | 14.78 | 0.98133 | 14.72 | 0.97694 | 14.654 | 0.97538 | 14.631 | 0.97669 | 14.65 | 0.97752 | 14.663 | 0.97912 | 14.687 | 0.98066 | 14.71 | 0.98066 | 14.71 | 0.98185 | 14.728 | 0.97961 | 14.694 | 0.9811 | 14.716
E.ALTAIR |  | 0.98231 | 14.735 | 0.98505 | 14.776 | 0.98679 | 14.802 | 0.98779 | 14.817 | 0.98839 | 14.826 | 0.98917 | 14.838 | 0.99001 | 14.85 | 0.99109 | 14.866 | 0.99049 | 14.857 | 0.98943 | 14.841 | 0.98741 | 14.811 | 0.98685 | 14.803 | 0.98478 | 14.772 | 0.98062 | 14.709 | 0.97607 | 14.641 | 0.97445 | 14.617 | 0.9758 | 14.637 | 0.97666 | 14.65 | 0.97833 | 14.675 | 0.97992 | 14.699 | 0.97992 | 14.699 | 0.98116 | 14.717 | 0.97883 | 14.682 | 0.98037 | 14.706
AGRICULTORES |  | 0.98228 | 14.734 | 0.98502 | 14.775 | 0.98677 | 14.801 | 0.98776 | 14.816 | 0.98836 | 14.825 | 0.98915 | 14.837 | 0.98999 | 14.85 | 0.99107 | 14.866 | 0.99047 | 14.857 | 0.98941 | 14.841 | 0.98739 | 14.811 | 0.98682 | 14.802 | 0.98475 | 14.771 | 0.98058 | 14.709 | 0.97602 | 14.64 | 0.97439 | 14.616 | 0.97575 | 14.636 | 0.97661 | 14.649 | 0.97828 | 14.674 | 0.97988 | 14.698 | 0.97988 | 14.698 | 0.98112 | 14.717 | 0.97878 | 14.682 | 0.98033 | 14.705
Nudo Slack. |  | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220
AGRICULTORES_2 |  | 0.98228 | 14.734 | 0.98502 | 14.775 | 0.98677 | 14.801 | 0.98776 | 14.816 | 0.98836 | 14.825 | 0.98915 | 14.837 | 0.98999 | 14.85 | 0.99107 | 14.866 | 0.99047 | 14.857 | 0.98941 | 14.841 | 0.98739 | 14.811 | 0.98682 | 14.802 | 0.98475 | 14.771 | 0.98058 | 14.709 | 0.97602 | 14.64 | 0.97439 | 14.616 | 0.97575 | 14.636 | 0.97661 | 14.649 | 0.97828 | 14.674 | 0.97988 | 14.698 | 0.97988 | 14.698 | 0.98112 | 14.717 | 0.97878 | 14.682 | 0.98033 | 14.705
E.SIRIO |  | 0.98228 | 14.734 | 0.98502 | 14.775 | 0.98677 | 14.801 | 0.98776 | 14.816 | 0.98836 | 14.825 | 0.98915 | 14.837 | 0.98999 | 14.85 | 0.99107 | 14.866 | 0.99047 | 14.857 | 0.98941 | 14.841 | 0.98739 | 14.811 | 0.98682 | 14.802 | 0.98475 | 14.771 | 0.98058 | 14.709 | 0.97602 | 14.64 | 0.97439 | 14.616 | 0.97575 | 14.636 | 0.97661 | 14.649 | 0.97828 | 14.674 | 0.97988 | 14.698 | 0.97988 | 14.698 | 0.98112 | 14.717 | 0.97878 | 14.682 | 0.98033 | 14.705
Mínimo |  | 0.98228 | 14.734 | 0.98502 | 14.775 | 0.98677 | 14.801 | 0.98776 | 14.816 | 0.98836 | 14.825 | 0.98915 | 14.837 | 0.98999 | 14.85 | 0.99107 | 14.866 | 0.99047 | 14.857 | 0.98941 | 14.841 | 0.98739 | 14.811 | 0.98682 | 14.802 | 0.98475 | 14.771 | 0.98058 | 14.709 | 0.97602 | 14.64 | 0.97439 | 14.616 | 0.97575 | 14.636 | 0.97661 | 14.649 | 0.97828 | 14.674 | 0.97988 | 14.698 | 0.97988 | 14.698 | 0.98112 | 14.717 | 0.97878 | 14.682 | 0.98033 | 14.705
|  |  | 0.98227 |  | 0.985 |  | 0.98673 |  | 0.98773 |  | 0.98833 |  | 0.98913 |  | 0.99 |  | 0.99107 |  | 0.99047 |  | 0.9894 |  | 0.9874 |  | 0.9868 |  | 0.98473 |  | 0.9806 |  | 0.976 |  | 0.9744 |  | 0.97573 |  | 0.9766 |  | 0.97827 |  | 0.97987 |  | 0.97987 |  | 0.98113 |  | 0.9788 |  | 0.98033 | 0.9744
AÑO 2
Bus Records |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
|  | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt
Empalme. |  | 0.99669 | 14.95 | 0.99728 | 14.959 | 0.9976 | 14.964 | 0.99772 | 14.966 | 0.99793 | 14.969 | 0.99807 | 14.971 | 0.99824 | 14.974 | 0.99828 | 14.974 | 0.99809 | 14.971 | 0.99784 | 14.968 | 0.99753 | 14.963 | 0.99726 | 14.959 | 0.99687 | 14.953 | 0.99604 | 14.941 | 0.99515 | 14.927 | 0.99476 | 14.921 | 0.99513 | 14.927 | 0.99531 | 14.93 | 0.99556 | 14.933 | 0.99605 | 14.941 | 0.99654 | 14.948 | 0.99632 | 14.945 | 0.99594 | 14.939 | 0.99624 | 14.944
CRAL.ACABOSE_1 |  | 0.98977 | 14.846 | 0.99172 | 14.876 | 0.99271 | 14.891 | 0.9933 | 14.899 | 0.99392 | 14.909 | 0.99436 | 14.915 | 0.99465 | 14.92 | 0.99453 | 14.918 | 0.99373 | 14.906 | 0.99275 | 14.891 | 0.99187 | 14.878 | 0.9906 | 14.859 | 0.98936 | 14.84 | 0.98665 | 14.8 | 0.98378 | 14.757 | 0.98222 | 14.733 | 0.98381 | 14.757 | 0.98441 | 14.766 | 0.98501 | 14.775 | 0.98705 | 14.806 | 0.98852 | 14.828 | 0.9881 | 14.821 | 0.9871 | 14.806 | 0.98807 | 14.821
CRAL.ACABOSE_2 |  | 0.98943 | 14.841 | 0.99145 | 14.872 | 0.99247 | 14.887 | 0.99308 | 14.896 | 0.99373 | 14.906 | 0.99418 | 14.913 | 0.99448 | 14.917 | 0.99435 | 14.915 | 0.99352 | 14.903 | 0.99251 | 14.888 | 0.9916 | 14.874 | 0.99028 | 14.854 | 0.989 | 14.835 | 0.98619 | 14.793 | 0.98323 | 14.749 | 0.98161 | 14.724 | 0.98326 | 14.749 | 0.98388 | 14.758 | 0.9845 | 14.768 | 0.98661 | 14.799 | 0.98814 | 14.822 | 0.9877 | 14.815 | 0.98667 | 14.8 | 0.98767 | 14.815
E.SIRIO_4 |  | 0.98904 | 14.836 | 0.99113 | 14.867 | 0.99219 | 14.883 | 0.99283 | 14.892 | 0.99351 | 14.903 | 0.99397 | 14.91 | 0.99428 | 14.914 | 0.99413 | 14.912 | 0.99327 | 14.899 | 0.99222 | 14.883 | 0.99128 | 14.869 | 0.9899 | 14.849 | 0.98858 | 14.829 | 0.98566 | 14.785 | 0.98259 | 14.739 | 0.98091 | 14.714 | 0.98262 | 14.739 | 0.98327 | 14.749 | 0.98391 | 14.759 | 0.9861 | 14.792 | 0.98769 | 14.815 | 0.98724 | 14.809 | 0.98617 | 14.793 | 0.98721 | 14.808
E.SIRIO_1 |  | 0.98423 | 14.763 | 0.98679 | 14.802 | 0.98822 | 14.823 | 0.98904 | 14.836 | 0.98966 | 14.845 | 0.99036 | 14.855 | 0.99149 | 14.872 | 0.99206 | 14.881 | 0.99141 | 14.871 | 0.99054 | 14.858 | 0.98877 | 14.832 | 0.98822 | 14.823 | 0.98637 | 14.796 | 0.98265 | 14.74 | 0.97857 | 14.679 | 0.97711 | 14.657 | 0.97834 | 14.675 | 0.97912 | 14.687 | 0.9806 | 14.709 | 0.98211 | 14.732 | 0.98459 | 14.769 | 0.98315 | 14.747 | 0.9811 | 14.716 | 0.98248 | 14.737
E.SIRIO_2 |  | 0.98374 | 14.756 | 0.98639 | 14.796 | 0.98786 | 14.818 | 0.9887 | 14.831 | 0.98934 | 14.84 | 0.99006 | 14.851 | 0.99123 | 14.868 | 0.99181 | 14.877 | 0.99115 | 14.867 | 0.99025 | 14.854 | 0.98843 | 14.827 | 0.98787 | 14.818 | 0.98597 | 14.789 | 0.98213 | 14.732 | 0.97793 | 14.669 | 0.97643 | 14.646 | 0.97769 | 14.665 | 0.97849 | 14.677 | 0.98002 | 14.7 | 0.98156 | 14.723 | 0.98413 | 14.762 | 0.98264 | 14.74 | 0.98052 | 14.708 | 0.98195 | 14.729
E.SIRIO_3 |  | 0.98278 | 14.742 | 0.98557 | 14.784 | 0.98713 | 14.807 | 0.98803 | 14.82 | 0.9887 | 14.831 | 0.98946 | 14.842 | 0.99071 | 14.861 | 0.99133 | 14.87 | 0.99063 | 14.859 | 0.98969 | 14.845 | 0.98776 | 14.816 | 0.98718 | 14.808 | 0.98515 | 14.777 | 0.9811 | 14.717 | 0.97665 | 14.65 | 0.97506 | 14.626 | 0.9764 | 14.646 | 0.97724 | 14.659 | 0.97886 | 14.683 | 0.98049 | 14.707 | 0.9832 | 14.748 | 0.98163 | 14.724 | 0.97937 | 14.691 | 0.98089 | 14.713
I.E.S.J.VERNE |  | 0.98212 | 14.732 | 0.98501 | 14.775 | 0.98663 | 14.8 | 0.98757 | 14.813 | 0.98826 | 14.824 | 0.98905 | 14.836 | 0.99035 | 14.855 | 0.991 | 14.865 | 0.99027 | 14.854 | 0.9893 | 14.839 | 0.98729 | 14.809 | 0.98669 | 14.8 | 0.98459 | 14.769 | 0.98039 | 14.706 | 0.97576 | 14.636 | 0.97412 | 14.612 | 0.9755 | 14.632 | 0.97638 | 14.646 | 0.97806 | 14.671 | 0.97974 | 14.696 | 0.98257 | 14.738 | 0.98092 | 14.714 | 0.97858 | 14.679 | 0.98015 | 14.702
E.ALTAIR |  | 0.98142 | 14.721 | 0.98443 | 14.766 | 0.98611 | 14.792 | 0.98709 | 14.806 | 0.9878 | 14.817 | 0.98862 | 14.829 | 0.98997 | 14.85 | 0.99065 | 14.86 | 0.9899 | 14.849 | 0.98889 | 14.833 | 0.9868 | 14.802 | 0.98619 | 14.793 | 0.98401 | 14.76 | 0.97964 | 14.695 | 0.97484 | 14.623 | 0.97314 | 14.597 | 0.97457 | 14.619 | 0.97548 | 14.632 | 0.97723 | 14.658 | 0.97896 | 14.684 | 0.9819 | 14.729 | 0.98019 | 14.703 | 0.97776 | 14.666 | 0.97939 | 14.691
AGRICULTORES |  | 0.98138 | 14.721 | 0.9844 | 14.766 | 0.98608 | 14.791 | 0.98706 | 14.806 | 0.98778 | 14.817 | 0.9886 | 14.829 | 0.98995 | 14.849 | 0.99063 | 14.86 | 0.98988 | 14.848 | 0.98887 | 14.833 | 0.98677 | 14.802 | 0.98616 | 14.792 | 0.98398 | 14.76 | 0.9796 | 14.694 | 0.97479 | 14.622 | 0.97309 | 14.596 | 0.97451 | 14.618 | 0.97543 | 14.631 | 0.97718 | 14.658 | 0.97892 | 14.684 | 0.98186 | 14.728 | 0.98015 | 14.702 | 0.97771 | 14.666 | 0.97935 | 14.69
Nudo Slack. |  | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220
AGRICULTORES_2 |  | 0.98138 | 14.721 | 0.9844 | 14.766 | 0.98608 | 14.791 | 0.98706 | 14.806 | 0.98778 | 14.817 | 0.9886 | 14.829 | 0.98995 | 14.849 | 0.99063 | 14.86 | 0.98988 | 14.848 | 0.98887 | 14.833 | 0.98677 | 14.802 | 0.98616 | 14.792 | 0.98398 | 14.76 | 0.9796 | 14.694 | 0.97479 | 14.622 | 0.97309 | 14.596 | 0.97451 | 14.618 | 0.97543 | 14.631 | 0.97718 | 14.658 | 0.97892 | 14.684 | 0.98186 | 14.728 | 0.98015 | 14.702 | 0.97771 | 14.666 | 0.97935 | 14.69
E.SIRIO |  | 0.98138 | 14.721 | 0.9844 | 14.766 | 0.98608 | 14.791 | 0.98706 | 14.806 | 0.98778 | 14.817 | 0.9886 | 14.829 | 0.98995 | 14.849 | 0.99063 | 14.86 | 0.98988 | 14.848 | 0.98887 | 14.833 | 0.98677 | 14.802 | 0.98616 | 14.792 | 0.98398 | 14.76 | 0.9796 | 14.694 | 0.97479 | 14.622 | 0.97309 | 14.596 | 0.97451 | 14.618 | 0.97543 | 14.631 | 0.97718 | 14.658 | 0.97892 | 14.684 | 0.98186 | 14.728 | 0.98015 | 14.702 | 0.97771 | 14.666 | 0.97935 | 14.69
Mínimo |  | 0.98138 | 14.721 | 0.9844 | 14.766 | 0.98608 | 14.791 | 0.98706 | 14.806 | 0.98778 | 14.817 | 0.9886 | 14.829 | 0.98995 | 14.849 | 0.99063 | 14.86 | 0.98988 | 14.848 | 0.98887 | 14.833 | 0.98677 | 14.802 | 0.98616 | 14.792 | 0.98398 | 14.76 | 0.9796 | 14.694 | 0.97479 | 14.622 | 0.97309 | 14.596 | 0.97451 | 14.618 | 0.97543 | 14.631 | 0.97718 | 14.658 | 0.97892 | 14.684 | 0.98186 | 14.728 | 0.98015 | 14.702 | 0.97771 | 14.666 | 0.97935 | 14.69
|  |  | 0.9814 |  | 0.9844 |  | 0.98607 |  | 0.98707 |  | 0.9878 |  | 0.9886 |  | 0.98993 |  | 0.99067 |  | 0.98987 |  | 0.98887 |  | 0.9868 |  | 0.98613 |  | 0.984 |  | 0.9796 |  | 0.9748 |  | 0.97307 |  | 0.97453 |  | 0.9754 |  | 0.9772 |  | 0.97893 |  | 0.98187 |  | 0.98013 |  | 0.97773 |  | 0.97933 | 0.97307
AÑO 3
|  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
|  | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV)
Empalme. |  | 0.99653 | 14.948 | 0.99714 | 14.957 | 0.99748 | 14.962 | 0.9977 | 14.966 | 0.99783 | 14.967 | 0.99798 | 14.97 | 0.9981 | 14.971 | 0.9982 | 14.973 | 0.99799 | 14.97 | 0.99774 | 14.966 | 0.99737 | 14.961 | 0.99707 | 14.956 | 0.99664 | 14.95 | 0.99584 | 14.938 | 0.99491 | 14.924 | 0.99449 | 14.917 | 0.99489 | 14.923 | 0.99512 | 14.927 | 0.99534 | 14.93 | 0.99582 | 14.937 | 0.99637 | 14.945 | 0.99613 | 14.942 | 0.99573 | 14.936 | 0.99605 | 14.941
CRAL.ACABOSE_1 |  | 0.98925 | 14.839 | 0.9913 | 14.869 | 0.99246 | 14.887 | 0.99322 | 14.898 | 0.99362 | 14.904 | 0.99407 | 14.911 | 0.99433 | 14.915 | 0.99425 | 14.914 | 0.99341 | 14.901 | 0.99249 | 14.887 | 0.99139 | 14.871 | 0.98999 | 14.85 | 0.98876 | 14.831 | 0.98597 | 14.79 | 0.98296 | 14.744 | 0.98132 | 14.72 | 0.98299 | 14.745 | 0.98386 | 14.758 | 0.98425 | 14.764 | 0.98631 | 14.795 | 0.98794 | 14.819 | 0.98749 | 14.812 | 0.98644 | 14.797 | 0.98746 | 14.812
CRAL.ACABOSE_2 |  | 0.98889 | 14.833 | 0.99101 | 14.865 | 0.99221 | 14.883 | 0.993 | 14.895 | 0.99342 | 14.901 | 0.99389 | 14.908 | 0.99415 | 14.912 | 0.99406 | 14.911 | 0.99319 | 14.898 | 0.99223 | 14.883 | 0.9911 | 14.866 | 0.98965 | 14.845 | 0.98838 | 14.826 | 0.98549 | 14.782 | 0.98238 | 14.736 | 0.98068 | 14.71 | 0.98241 | 14.736 | 0.98332 | 14.75 | 0.98372 | 14.756 | 0.98585 | 14.788 | 0.98753 | 14.813 | 0.98708 | 14.806 | 0.98599 | 14.79 | 0.98704 | 14.806
E.SIRIO_4 |  | 0.98848 | 14.827 | 0.99068 | 14.86 | 0.99193 | 14.879 | 0.99275 | 14.891 | 0.99318 | 14.898 | 0.99367 | 14.905 | 0.99393 | 14.909 | 0.99384 | 14.908 | 0.99293 | 14.894 | 0.99193 | 14.879 | 0.99076 | 14.861 | 0.98925 | 14.839 | 0.98794 | 14.819 | 0.98494 | 14.774 | 0.98171 | 14.726 | 0.97994 | 14.699 | 0.98174 | 14.726 | 0.98269 | 14.74 | 0.98309 | 14.746 | 0.98531 | 14.78 | 0.98706 | 14.806 | 0.98659 | 14.799 | 0.98547 | 14.782 | 0.98656 | 14.798
E.SIRIO_1 |  | 0.98342 | 14.751 | 0.98612 | 14.792 | 0.98763 | 14.814 | 0.98861 | 14.829 | 0.98914 | 14.837 | 0.98988 | 14.848 | 0.99064 | 14.86 | 0.99166 | 14.875 | 0.99097 | 14.865 | 0.99007 | 14.851 | 0.98818 | 14.823 | 0.98742 | 14.811 | 0.98547 | 14.782 | 0.98177 | 14.727 | 0.97748 | 14.662 | 0.97594 | 14.639 | 0.97724 | 14.659 | 0.9781 | 14.671 | 0.97962 | 14.694 | 0.98114 | 14.717 | 0.9838 | 14.757 | 0.9823 | 14.734 | 0.98013 | 14.702 | 0.98159 | 14.724
E.SIRIO_2 |  | 0.98292 | 14.744 | 0.98569 | 14.785 | 0.98725 | 14.809 | 0.98825 | 14.824 | 0.9888 | 14.832 | 0.98956 | 14.843 | 0.99036 | 14.855 | 0.9914 | 14.871 | 0.9907 | 14.861 | 0.98977 | 14.847 | 0.98782 | 14.817 | 0.98704 | 14.806 | 0.98504 | 14.776 | 0.98123 | 14.718 | 0.9768 | 14.652 | 0.97522 | 14.628 | 0.97656 | 14.648 | 0.97744 | 14.662 | 0.97901 | 14.685 | 0.98057 | 14.709 | 0.98332 | 14.75 | 0.98176 | 14.726 | 0.97952 | 14.693 | 0.98103 | 14.715
E.SIRIO_3 |  | 0.9819 | 14.729 | 0.98484 | 14.773 | 0.98649 | 14.797 | 0.98755 | 14.813 | 0.98813 | 14.822 | 0.98894 | 14.834 | 0.98978 | 14.847 | 0.9909 | 14.863 | 0.99016 | 14.852 | 0.98918 | 14.838 | 0.98711 | 14.807 | 0.9863 | 14.794 | 0.98417 | 14.762 | 0.98014 | 14.702 | 0.97546 | 14.632 | 0.97379 | 14.607 | 0.97519 | 14.628 | 0.97612 | 14.642 | 0.97779 | 14.667 | 0.97943 | 14.692 | 0.98234 | 14.735 | 0.98069 | 14.71 | 0.97832 | 14.675 | 0.97992 | 14.699
I.E.S.J.VERNE |  | 0.9812 | 14.718 | 0.98425 | 14.764 | 0.98597 | 14.789 | 0.98707 | 14.806 | 0.98767 | 14.815 | 0.98851 | 14.828 | 0.98938 | 14.841 | 0.99055 | 14.858 | 0.98979 | 14.847 | 0.98877 | 14.832 | 0.98662 | 14.799 | 0.98578 | 14.787 | 0.98355 | 14.753 | 0.97939 | 14.691 | 0.97453 | 14.618 | 0.9728 | 14.592 | 0.97425 | 14.614 | 0.97522 | 14.628 | 0.97695 | 14.654 | 0.97865 | 14.68 | 0.98167 | 14.725 | 0.97995 | 14.699 | 0.97748 | 14.662 | 0.97914 | 14.687
E.ALTAIR |  | 0.98048 | 14.707 | 0.98364 | 14.755 | 0.98542 | 14.781 | 0.98657 | 14.798 | 0.98719 | 14.808 | 0.98806 | 14.821 | 0.98897 | 14.834 | 0.99018 | 14.853 | 0.9894 | 14.841 | 0.98834 | 14.825 | 0.98611 | 14.792 | 0.98524 | 14.779 | 0.98291 | 14.744 | 0.97861 | 14.679 | 0.97356 | 14.603 | 0.97177 | 14.577 | 0.97327 | 14.599 | 0.97427 | 14.614 | 0.97608 | 14.641 | 0.97784 | 14.668 | 0.98098 | 14.715 | 0.97918 | 14.688 | 0.97662 | 14.649 | 0.97834 | 14.675
AGRICULTORES |  | 0.98044 | 14.707 | 0.9836 | 14.754 | 0.98539 | 14.781 | 0.98654 | 14.798 | 0.98716 | 14.807 | 0.98803 | 14.82 | 0.98894 | 14.834 | 0.99016 | 14.852 | 0.98937 | 14.841 | 0.98832 | 14.825 | 0.98608 | 14.791 | 0.98521 | 14.778 | 0.98287 | 14.743 | 0.97856 | 14.678 | 0.9735 | 14.603 | 0.97171 | 14.576 | 0.97321 | 14.598 | 0.97422 | 14.613 | 0.97603 | 14.64 | 0.97779 | 14.667 | 0.98094 | 14.714 | 0.97914 | 14.687 | 0.97657 | 14.649 | 0.97829 | 14.674
Nudo Slack. |  | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220
AGRICULTORES_2 |  | 0.98044 | 14.707 | 0.9836 | 14.754 | 0.98539 | 14.781 | 0.98654 | 14.798 | 0.98716 | 14.807 | 0.98803 | 14.82 | 0.98894 | 14.834 | 0.99016 | 14.852 | 0.98937 | 14.841 | 0.98832 | 14.825 | 0.98608 | 14.791 | 0.98521 | 14.778 | 0.98287 | 14.743 | 0.97856 | 14.678 | 0.9735 | 14.603 | 0.97171 | 14.576 | 0.97321 | 14.598 | 0.97422 | 14.613 | 0.97603 | 14.64 | 0.97779 | 14.667 | 0.98094 | 14.714 | 0.97914 | 14.687 | 0.97657 | 14.649 | 0.97829 | 14.674
E.SIRIO |  | 0.98044 | 14.707 | 0.9836 | 14.754 | 0.98539 | 14.781 | 0.98654 | 14.798 | 0.98716 | 14.807 | 0.98803 | 14.82 | 0.98894 | 14.834 | 0.99016 | 14.852 | 0.98937 | 14.841 | 0.98832 | 14.825 | 0.98608 | 14.791 | 0.98521 | 14.778 | 0.98287 | 14.743 | 0.97856 | 14.678 | 0.9735 | 14.603 | 0.97171 | 14.576 | 0.97321 | 14.598 | 0.97422 | 14.613 | 0.97603 | 14.64 | 0.97779 | 14.667 | 0.98094 | 14.714 | 0.97914 | 14.687 | 0.97657 | 14.649 | 0.97829 | 14.674
Mínimo |  | 0.98044 | 14.707 | 0.9836 | 14.754 | 0.98539 | 14.781 | 0.98654 | 14.798 | 0.98716 | 14.807 | 0.98803 | 14.82 | 0.98894 | 14.834 | 0.99016 | 14.852 | 0.98937 | 14.841 | 0.98832 | 14.825 | 0.98608 | 14.791 | 0.98521 | 14.778 | 0.98287 | 14.743 | 0.97856 | 14.678 | 0.9735 | 14.603 | 0.97171 | 14.576 | 0.97321 | 14.598 | 0.97422 | 14.613 | 0.97603 | 14.64 | 0.97779 | 14.667 | 0.98094 | 14.714 | 0.97914 | 14.687 | 0.97657 | 14.649 | 0.97829 | 14.674 | 0.97171
Hora 16 | Año 0 | Año 1 | Año 2 | Año 3
Tensión Pu | 0.97553 | 0.97439 | 0.97309 | 0.97171
Tensión (kV) | 14.633 | 14.616 | 14.596 | 14.576
AÑO 3 CON DISP. AL 25% | [13 empty] | AÑO 3 CON DISP. AL 25% | [13 empty] | AÑO 3 CON DISP. AL 25%
| 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
|  |  | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV)
Empalme. |  |  | 0.99711 | 14.957 | 0.99745 | 14.962 | 0.99767 | 14.965 | 0.9978 | 14.967 | 0.99795 | 14.969 | 0.99807 | 14.971 | 0.99817 | 14.973 | 0.99796 | 14.969 | 0.99771 | 14.966 | 0.99734 | 14.96 | 0.99709 | 14.956 |  |  | 0.99587 | 14.938 | 0.99494 | 14.924 | 0.99451 | 14.918 | 0.99491 | 14.924 | 0.9951 | 14.926 | 0.99542 | 14.931 | 0.99585 | 14.938 |  |  | 0.99616 | 14.942 | 15 | 0.99576 | 0.99608 | 14.941
CRAL.ACABOSE_1 |  |  | 0.991 | 14.865 | 0.99216 | 14.882 | 0.99292 | 14.894 | 0.99332 | 14.9 | 0.99378 | 14.907 | 0.99403 | 14.91 | 0.99395 | 14.909 | 0.99311 | 14.897 | 0.99209 | 14.881 | 0.99109 | 14.866 | 0.98981 | 14.847 |  |  | 0.98624 | 14.794 | 0.98323 | 14.748 | 0.98159 | 14.724 | 0.98326 | 14.749 | 0.98385 | 14.758 | 0.98459 | 14.769 | 0.98658 | 14.799 |  |  | 0.98776 | 14.816 | 15 | 0.98671 | 0.98773 | 14.816
CRAL.ACABOSE_2 |  |  | 0.9907 | 14.861 | 0.9919 | 14.879 | 0.99269 | 14.89 | 0.99311 | 14.897 | 0.99358 | 14.904 | 0.99384 | 14.908 | 0.99375 | 14.906 | 0.99288 | 14.893 | 0.99182 | 14.877 | 0.99079 | 14.862 | 0.98946 | 14.842 |  |  | 0.98577 | 14.787 | 0.98266 | 14.74 | 0.98096 | 14.714 | 0.98269 | 14.74 | 0.98331 | 14.75 | 0.98406 | 14.761 | 0.98613 | 14.792 |  |  | 0.98735 | 14.81 | 15 | 0.98627 | 0.98732 | 14.81
E.SIRIO_4 |  |  | 0.99036 | 14.855 | 0.99161 | 14.874 | 0.99243 | 14.886 | 0.99286 | 14.893 | 0.99335 | 14.9 | 0.99362 | 14.904 | 0.99352 | 14.903 | 0.99261 | 14.889 | 0.99151 | 14.873 | 0.99044 | 14.857 | 0.98906 | 14.836 |  |  | 0.98523 | 14.778 | 0.982 | 14.73 | 0.98023 | 14.703 | 0.98203 | 14.73 | 0.98267 | 14.74 | 0.98345 | 14.752 | 0.9856 | 14.784 |  |  | 0.98688 | 14.803 | 15 | 0.98576 | 0.98685 | 14.803
E.SIRIO_1 |  |  | 0.98507 | 14.776 | 0.98659 | 14.799 | 0.98756 | 14.813 | 0.98809 | 14.821 | 0.98883 | 14.833 | 0.98962 | 14.844 | 0.99061 | 14.859 | 0.98993 | 14.849 | 0.98902 | 14.835 | 0.98713 | 14.807 | 0.98658 | 14.799 |  |  | 0.98271 | 14.741 | 0.97842 | 14.676 | 0.97688 | 14.653 | 0.97818 | 14.673 | 0.97899 | 14.685 | 0.98316 | 14.747 | 0.98207 | 14.731 |  |  | 0.98323 | 14.748 | 15 | 0.98107 | 0.98253 | 14.738
E.SIRIO_2 |  |  | 0.98461 | 14.769 | 0.98617 | 14.792 | 0.98717 | 14.808 | 0.98772 | 14.816 | 0.98848 | 14.827 | 0.98929 | 14.839 | 0.99032 | 14.855 | 0.98962 | 14.844 | 0.98869 | 14.83 | 0.98674 | 14.801 | 0.98617 | 14.793 |  |  | 0.9822 | 14.733 | 0.97777 | 14.667 | 0.9762 | 14.643 | 0.97753 | 14.663 | 0.97836 | 14.675 | 0.98269 | 14.74 | 0.98154 | 14.723 |  |  | 0.98273 | 14.741 | 15 | 0.9805 | 0.982 | 14.73
E.SIRIO_3 |  |  | 0.98365 | 14.755 | 0.9853 | 14.78 | 0.98637 | 14.796 | 0.98695 | 14.804 | 0.98776 | 14.816 | 0.98862 | 14.829 | 0.98972 | 14.846 | 0.98898 | 14.835 | 0.98799 | 14.82 | 0.98593 | 14.789 | 0.98534 | 14.78 |  |  | 0.9812 | 14.718 | 0.97652 | 14.648 | 0.97485 | 14.623 | 0.97625 | 14.644 | 0.97714 | 14.657 | 0.9819 | 14.729 | 0.98049 | 14.707 |  |  | 0.98175 | 14.726 | 15 | 0.97938 | 0.98097 | 14.715
I.E.S.J.VERNE |  |  | 0.98296 | 14.744 | 0.98468 | 14.77 | 0.98579 | 14.787 | 0.98638 | 14.796 | 0.98722 | 14.808 | 0.98812 | 14.822 | 0.98927 | 14.839 | 0.9885 | 14.828 | 0.98748 | 14.812 | 0.98534 | 14.78 | 0.98473 | 14.771 |  |  | 0.98054 | 14.708 | 0.97568 | 14.635 | 0.97395 | 14.609 | 0.9754 | 14.631 | 0.97632 | 14.645 | 0.98115 | 14.717 | 0.9798 | 14.697 |  |  | 0.9811 | 14.716 | 15 | 0.97864 | 0.98029 | 14.704
E.ALTAIR |  |  | 0.98227 | 14.734 | 0.98405 | 14.761 | 0.9852 | 14.778 | 0.98582 | 14.787 | 0.98669 | 14.8 | 0.98763 | 14.814 | 0.98882 | 14.832 | 0.98803 | 14.821 | 0.98698 | 14.805 | 0.98475 | 14.771 | 0.98412 | 14.762 |  |  | 0.97983 | 14.697 | 0.97478 | 14.622 | 0.973 | 14.595 | 0.97449 | 14.617 | 0.97545 | 14.632 | 0.98035 | 14.705 | 0.97906 | 14.686 |  |  | 0.9804 | 14.706 | 15 | 0.97784 | 0.97956 | 14.693
AGRICULTORES |  |  | 0.98223 | 14.733 | 0.98401 | 14.76 | 0.98516 | 14.777 | 0.98579 | 14.787 | 0.98666 | 14.8 | 0.9876 | 14.814 | 0.98879 | 14.832 | 0.988 | 14.82 | 0.98694 | 14.804 | 0.98471 | 14.771 | 0.98408 | 14.761 |  |  | 0.97979 | 14.697 | 0.97473 | 14.621 | 0.97294 | 14.594 | 0.97444 | 14.617 | 0.9754 | 14.631 | 0.98031 | 14.705 | 0.97902 | 14.685 |  |  | 0.98037 | 14.705 | 15 | 0.9778 | 0.97952 | 14.693
Nudo Slack. |  |  | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 |  |  | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 |  |  | 1 | 220 | 220 | 1 | 1 | 220
AGRICULTORES_2 |  |  | 0.98222 | 14.733 | 0.98401 | 14.76 | 0.98516 | 14.777 | 0.98578 | 14.787 | 0.98665 | 14.8 | 0.98759 | 14.814 | 0.98879 | 14.832 | 0.988 | 14.82 | 0.98694 | 14.804 | 0.9847 | 14.771 | 0.98407 | 14.761 |  |  | 0.9798 | 14.697 | 0.97474 | 14.621 | 0.97295 | 14.594 | 0.97445 | 14.617 | 0.97541 | 14.631 | 0.98032 | 14.705 | 0.97902 | 14.685 |  |  | 0.98037 | 14.706 | 15 | 0.97781 | 0.97953 | 14.693
E.SIRIO |  |  | 0.98221 | 14.733 | 0.98399 | 14.76 | 0.98514 | 14.777 | 0.98577 | 14.786 | 0.98664 | 14.8 | 0.98758 | 14.814 | 0.98877 | 14.832 | 0.98798 | 14.82 | 0.98692 | 14.804 | 0.98469 | 14.77 | 0.98406 | 14.761 |  |  | 0.97981 | 14.697 | 0.97475 | 14.621 | 0.97296 | 14.594 | 0.97446 | 14.617 | 0.97542 | 14.631 | 0.98033 | 14.705 | 0.97903 | 14.686 |  |  | 0.98038 | 14.706 | 15 | 0.97782 | 0.97954 | 14.693
AÑO 3 CON DISP. AL 50% | [13 empty] | AÑO 3 CON DISP. AL 50% | [13 empty] | AÑO 3 CON DISP. AL 50% | [13 empty] | AÑO 3 CON DISP. AL 50%
| 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24 |  |  | Bus Records
|  |  | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) |  | PU Volt | Volt (kV)
Empalme. |  |  | 0.99708 | 14.956 | 0.99742 | 14.961 | 0.99764 | 14.965 | 0.99777 | 14.967 | 0.99792 | 14.969 | 0.99804 | 14.971 | 0.99814 | 14.972 | 0.99793 | 14.969 | 0.99768 | 14.965 | 0.99732 | 14.96 | 0.99706 | 14.956 |  |  | 0.99589 | 14.938 | 0.99496 | 14.924 | 0.99454 | 14.918 | 0.99494 | 14.924 | 0.99513 | 14.927 | 0.99545 | 14.932 | 0.99588 | 14.938 |  |  | 0.99619 | 14.943 | 0.99579 | 14.937 | 0.9961 | 14.942
CRAL.ACABOSE_1 |  |  | 0.9907 | 14.86 | 0.99186 | 14.878 | 0.99262 | 14.889 | 0.99302 | 14.895 | 0.99348 | 14.902 | 0.99373 | 14.906 | 0.99365 | 14.905 | 0.99281 | 14.892 | 0.99179 | 14.877 | 0.99079 | 14.862 | 0.98951 | 14.843 |  |  | 0.98651 | 14.798 | 0.9835 | 14.753 | 0.98186 | 14.728 | 0.98353 | 14.753 | 0.98413 | 14.762 | 0.98486 | 14.773 | 0.98685 | 14.803 |  |  | 0.98804 | 14.821 | 0.98699 | 14.805 | 0.988 | 14.82
CRAL.ACABOSE_2 |  |  | 0.99039 | 14.856 | 0.99159 | 14.874 | 0.99238 | 14.886 | 0.9928 | 14.892 | 0.99327 | 14.899 | 0.99353 | 14.903 | 0.99344 | 14.902 | 0.99257 | 14.889 | 0.99151 | 14.873 | 0.99048 | 14.857 | 0.98915 | 14.837 |  |  | 0.98606 | 14.791 | 0.98295 | 14.744 | 0.98125 | 14.719 | 0.98298 | 14.745 | 0.98359 | 14.754 | 0.98435 | 14.765 | 0.98641 | 14.796 |  |  | 0.98764 | 14.815 | 0.98656 | 14.798 | 0.98761 | 14.814
E.SIRIO_4 |  |  | 0.99004 | 14.851 | 0.99129 | 14.869 | 0.99211 | 14.882 | 0.99254 | 14.888 | 0.99303 | 14.895 | 0.9933 | 14.899 | 0.9932 | 14.898 | 0.99229 | 14.884 | 0.99119 | 14.868 | 0.99012 | 14.852 | 0.98874 | 14.831 |  |  | 0.98552 | 14.783 | 0.98229 | 14.734 | 0.98052 | 14.708 | 0.98233 | 14.735 | 0.98296 | 14.744 | 0.98374 | 14.756 | 0.98589 | 14.788 |  |  | 0.98717 | 14.808 | 0.98605 | 14.791 | 0.98714 | 14.807
E.SIRIO_1 |  |  | 0.98402 | 14.76 | 0.98554 | 14.783 | 0.98652 | 14.798 | 0.98705 | 14.806 | 0.98779 | 14.817 | 0.98857 | 14.829 | 0.98957 | 14.844 | 0.98889 | 14.833 | 0.98798 | 14.82 | 0.98609 | 14.791 | 0.98553 | 14.783 |  |  | 0.98366 | 14.755 | 0.97938 | 14.691 | 0.97784 | 14.668 | 0.97914 | 14.687 | 0.97995 | 14.699 | 0.98412 | 14.762 | 0.98303 | 14.745 |  |  | 0.98419 | 14.763 | 0.98203 | 14.73 | 0.98349 | 14.752
E.SIRIO_2 |  |  | 0.98352 | 14.753 | 0.98508 | 14.776 | 0.98609 | 14.791 | 0.98664 | 14.8 | 0.9874 | 14.811 | 0.98821 | 14.823 | 0.98924 | 14.839 | 0.98854 | 14.828 | 0.98761 | 14.814 | 0.98566 | 14.785 | 0.98509 | 14.776 |  |  | 0.98319 | 14.748 | 0.97877 | 14.682 | 0.97719 | 14.658 | 0.97852 | 14.678 | 0.97936 | 14.69 | 0.98368 | 14.755 | 0.98253 | 14.738 |  |  | 0.98372 | 14.756 | 0.98149 | 14.722 | 0.98299 | 14.745
E.SIRIO_3 |  |  | 0.98247 | 14.737 | 0.98412 | 14.762 | 0.98518 | 14.778 | 0.98576 | 14.786 | 0.98657 | 14.799 | 0.98743 | 14.812 | 0.98854 | 14.828 | 0.9878 | 14.817 | 0.98681 | 14.802 | 0.98474 | 14.771 | 0.98415 | 14.762 |  |  | 0.98228 | 14.734 | 0.97761 | 14.664 | 0.97594 | 14.639 | 0.97734 | 14.66 | 0.97823 | 14.673 | 0.98299 | 14.745 | 0.98158 | 14.724 |  |  | 0.98283 | 14.742 | 0.98047 | 14.707 | 0.98206 | 14.731
I.E.S.J.VERNE |  |  | 0.98168 | 14.725 | 0.98339 | 14.751 | 0.9845 | 14.768 | 0.9851 | 14.777 | 0.98594 | 14.789 | 0.98684 | 14.803 | 0.98799 | 14.82 | 0.98722 | 14.808 | 0.9862 | 14.793 | 0.98405 | 14.761 | 0.98345 | 14.752 |  |  | 0.98171 | 14.726 | 0.97686 | 14.653 | 0.97513 | 14.627 | 0.97658 | 14.649 | 0.9775 | 14.662 | 0.98233 | 14.735 | 0.98097 | 14.715 |  |  | 0.98227 | 14.734 | 0.97981 | 14.697 | 0.98147 | 14.722
E.ALTAIR |  |  | 0.9809 | 14.714 | 0.98269 | 14.74 | 0.98384 | 14.758 | 0.98446 | 14.767 | 0.98533 | 14.78 | 0.98627 | 14.794 | 0.98746 | 14.812 | 0.98667 | 14.8 | 0.98562 | 14.784 | 0.98338 | 14.751 | 0.98276 | 14.741 |  |  | 0.98108 | 14.716 | 0.97604 | 14.641 | 0.97425 | 14.614 | 0.97575 | 14.636 | 0.9767 | 14.651 | 0.98161 | 14.724 | 0.98031 | 14.705 |  |  | 0.98165 | 14.725 | 0.9791 | 14.686 | 0.98081 | 14.712
AGRICULTORES |  |  | 0.98085 | 14.713 | 0.98264 | 14.74 | 0.98379 | 14.757 | 0.98441 | 14.766 | 0.98529 | 14.779 | 0.98623 | 14.793 | 0.98742 | 14.811 | 0.98663 | 14.8 | 0.98557 | 14.784 | 0.98334 | 14.75 | 0.98271 | 14.741 |  |  | 0.98105 | 14.716 | 0.976 | 14.64 | 0.97421 | 14.613 | 0.97571 | 14.636 | 0.97666 | 14.65 | 0.98157 | 14.724 | 0.98027 | 14.704 |  |  | 0.98162 | 14.724 | 0.97906 | 14.686 | 0.98078 | 14.712
Nudo Slack. |  |  | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 |  |  | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 |  |  | 1 | 220 | 1 | 220 | 1 | 220
AGRICULTORES_2 |  |  | 0.98084 | 14.713 | 0.98263 | 14.739 | 0.98378 | 14.757 | 0.9844 | 14.766 | 0.98527 | 14.779 | 0.98621 | 14.793 | 0.98741 | 14.811 | 0.98662 | 14.799 | 0.98556 | 14.783 | 0.98332 | 14.75 | 0.9827 | 14.74 |  |  | 0.98106 | 14.716 | 0.97601 | 14.64 | 0.97422 | 14.613 | 0.97572 | 14.636 | 0.97667 | 14.65 | 0.98158 | 14.724 | 0.98028 | 14.704 |  |  | 0.98163 | 14.725 | 0.97907 | 14.686 | 0.98079 | 14.712
E.SIRIO |  |  | 0.98081 | 14.712 | 0.9826 | 14.739 | 0.98375 | 14.756 | 0.98437 | 14.766 | 0.98525 | 14.779 | 0.98619 | 14.793 | 0.98738 | 14.811 | 0.98659 | 14.799 | 0.98553 | 14.783 | 0.9833 | 14.749 | 0.98267 | 14.74 |  |  | 0.98108 | 14.716 | 0.97603 | 14.64 | 0.97424 | 14.614 | 0.97574 | 14.636 | 0.9767 | 14.65 | 0.98161 | 14.724 | 0.98031 | 14.705 |  |  | 0.98166 | 14.725 | 0.9791 | 14.686 | 0.98082 | 14.712
AÑO 3 CON DISP. AL 75% | [13 empty] | AÑO 3 CON DISP. AL 75% | [13 empty] | AÑO 3 CON DISP. AL 75% | [13 empty] | AÑO 3 CON DISP. AL 75%
| 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24 |  |  | Bus Records
|  |  | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) |  | PU Volt | Volt (kV)
Empalme. |  |  | 0.99711 | 14.957 | 0.99739 | 14.961 | 0.99762 | 14.964 | 0.99774 | 14.966 | 0.99789 | 14.968 | 0.99801 | 14.97 | 0.99811 | 14.972 | 0.9979 | 14.969 | 0.99765 | 14.965 | 0.99729 | 14.959 | 0.99703 | 14.955 |  |  | 0.99592 | 14.939 | 0.99499 | 14.925 | 0.99457 | 14.919 | 0.99497 | 14.925 | 0.99515 | 14.927 | 0.99547 | 14.932 | 0.9959 | 14.939 |  |  | 0.99621 | 14.943 | 0.99582 | 14.937 | 0.99613 | 14.942
CRAL.ACABOSE_1 |  |  | 0.991 | 14.865 | 0.99156 | 14.873 | 0.99233 | 14.885 | 0.99273 | 14.891 | 0.99318 | 14.898 | 0.99344 | 14.902 | 0.99336 | 14.9 | 0.99252 | 14.888 | 0.9915 | 14.872 | 0.9905 | 14.857 | 0.98922 | 14.838 |  |  | 0.98678 | 14.802 | 0.98377 | 14.757 | 0.98213 | 14.732 | 0.9838 | 14.757 | 0.9844 | 14.766 | 0.98513 | 14.777 | 0.98712 | 14.807 |  |  | 0.9883 | 14.825 | 0.98726 | 14.809 | 0.98827 | 14.824
CRAL.ACABOSE_2 |  |  | 0.9907 | 14.861 | 0.99129 | 14.869 | 0.99208 | 14.881 | 0.99249 | 14.887 | 0.99296 | 14.894 | 0.99323 | 14.898 | 0.99314 | 14.897 | 0.99227 | 14.884 | 0.99121 | 14.868 | 0.99017 | 14.853 | 0.98884 | 14.833 |  |  | 0.98634 | 14.795 | 0.98323 | 14.748 | 0.98153 | 14.723 | 0.98326 | 14.749 | 0.98387 | 14.758 | 0.98462 | 14.769 | 0.98669 | 14.8 |  |  | 0.98792 | 14.819 | 0.98684 | 14.803 | 0.98789 | 14.818
E.SIRIO_4 |  |  | 0.99036 | 14.855 | 0.99098 | 14.865 | 0.9918 | 14.877 | 0.99223 | 14.883 | 0.99272 | 14.891 | 0.99299 | 14.895 | 0.99289 | 14.893 | 0.99198 | 14.88 | 0.99088 | 14.863 | 0.98981 | 14.847 | 0.98842 | 14.826 |  |  | 0.9858 | 14.787 | 0.98258 | 14.739 | 0.98081 | 14.712 | 0.98261 | 14.739 | 0.98325 | 14.749 | 0.98403 | 14.76 | 0.98618 | 14.793 |  |  | 0.98746 | 14.812 | 0.98634 | 14.795 | 0.98743 | 14.811
E.SIRIO_1 |  |  | 0.98507 | 14.776 | 0.98452 | 14.768 | 0.98549 | 14.782 | 0.98603 | 14.79 | 0.98677 | 14.802 | 0.98755 | 14.813 | 0.98855 | 14.828 | 0.98787 | 14.818 | 0.98696 | 14.804 | 0.98507 | 14.776 | 0.98451 | 14.768 |  |  | 0.9846 | 14.769 | 0.98031 | 14.705 | 0.97878 | 14.682 | 0.98007 | 14.701 | 0.98089 | 14.713 | 0.98505 | 14.776 | 0.98397 | 14.759 |  |  | 0.98512 | 14.777 | 0.98296 | 14.744 | 0.98442 | 14.766
E.SIRIO_2 |  |  | 0.98461 | 14.769 | 0.98402 | 14.76 | 0.98503 | 14.775 | 0.98558 | 14.784 | 0.98634 | 14.795 | 0.98715 | 14.807 | 0.98819 | 14.823 | 0.98749 | 14.812 | 0.98655 | 14.798 | 0.9846 | 14.769 | 0.98403 | 14.76 |  |  | 0.98416 | 14.762 | 0.97974 | 14.696 | 0.97816 | 14.672 | 0.97949 | 14.692 | 0.98033 | 14.705 | 0.98465 | 14.77 | 0.9835 | 14.752 |  |  | 0.98469 | 14.77 | 0.98246 | 14.737 | 0.98396 | 14.759
E.SIRIO_3 |  |  | 0.98365 | 14.755 | 0.98296 | 14.744 | 0.98402 | 14.76 | 0.98461 | 14.769 | 0.98541 | 14.781 | 0.98628 | 14.794 | 0.98738 | 14.811 | 0.98664 | 14.8 | 0.98566 | 14.785 | 0.98359 | 14.754 | 0.983 | 14.745 |  |  | 0.98334 | 14.75 | 0.97867 | 14.68 | 0.97701 | 14.655 | 0.9784 | 14.676 | 0.97929 | 14.689 | 0.98405 | 14.761 | 0.98264 | 14.74 |  |  | 0.98389 | 14.758 | 0.98153 | 14.723 | 0.98312 | 14.747
I.E.S.J.VERNE |  |  | 0.98296 | 14.744 | 0.98214 | 14.732 | 0.98324 | 14.749 | 0.98385 | 14.758 | 0.98469 | 14.77 | 0.98559 | 14.784 | 0.98674 | 14.801 | 0.98597 | 14.79 | 0.98495 | 14.774 | 0.9828 | 14.742 | 0.98219 | 14.733 |  |  | 0.98286 | 14.743 | 0.97801 | 14.67 | 0.97629 | 14.644 | 0.97773 | 14.666 | 0.97865 | 14.68 | 0.98348 | 14.752 | 0.98212 | 14.732 |  |  | 0.98342 | 14.751 | 0.98096 | 14.714 | 0.98262 | 14.739
E.ALTAIR |  |  | 0.98227 | 14.734 | 0.98135 | 14.72 | 0.9825 | 14.738 | 0.98312 | 14.747 | 0.984 | 14.76 | 0.98493 | 14.774 | 0.98613 | 14.792 | 0.98534 | 14.78 | 0.98428 | 14.764 | 0.98205 | 14.731 | 0.98142 | 14.721 |  |  | 0.9823 | 14.734 | 0.97726 | 14.659 | 0.97548 | 14.632 | 0.97697 | 14.655 | 0.97793 | 14.669 | 0.98283 | 14.742 | 0.98153 | 14.723 |  |  | 0.98287 | 14.743 | 0.98032 | 14.705 | 0.98203 | 14.73
AGRICULTORES |  |  | 0.98223 | 14.733 | 0.98129 | 14.719 | 0.98245 | 14.737 | 0.98307 | 14.746 | 0.98394 | 14.759 | 0.98489 | 14.773 | 0.98609 | 14.791 | 0.9853 | 14.779 | 0.98424 | 14.764 | 0.98199 | 14.73 | 0.98137 | 14.721 |  |  | 0.98227 | 14.734 | 0.97723 | 14.658 | 0.97544 | 14.632 | 0.97694 | 14.654 | 0.97789 | 14.668 | 0.9828 | 14.742 | 0.9815 | 14.723 |  |  | 0.98285 | 14.743 | 0.98029 | 14.704 | 0.98201 | 14.73
Nudo Slack. |  |  | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 |  |  | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 |  |  | 1 | 220 | 1 | 220 | 1 | 220
AGRICULTORES_2 |  |  | 0.98222 | 14.733 | 0.98128 | 14.719 | 0.98243 | 14.736 | 0.98305 | 14.746 | 0.98393 | 14.759 | 0.98487 | 14.773 | 0.98607 | 14.791 | 0.98528 | 14.779 | 0.98422 | 14.763 | 0.98198 | 14.73 | 0.98135 | 14.72 |  |  | 0.98229 | 14.734 | 0.97724 | 14.659 | 0.97546 | 14.632 | 0.97695 | 14.654 | 0.97791 | 14.669 | 0.98282 | 14.742 | 0.98152 | 14.723 |  |  | 0.98287 | 14.743 | 0.98031 | 14.705 | 0.98203 | 14.73
E.SIRIO |  |  | 0.98221 | 14.733 | 0.98123 | 14.719 | 0.98239 | 14.736 | 0.98301 | 14.745 | 0.98388 | 14.758 | 0.98483 | 14.772 | 0.98603 | 14.79 | 0.98524 | 14.779 | 0.98417 | 14.763 | 0.98193 | 14.729 | 0.98131 | 14.72 |  |  | 0.98233 | 14.735 | 0.97728 | 14.659 | 0.97549 | 14.632 | 0.97699 | 14.655 | 0.97795 | 14.669 | 0.98286 | 14.743 | 0.98156 | 14.723 |  |  | 0.9829 | 14.744 | 0.98034 | 14.705 | 0.98206 | 14.731
AÑO 3 CON DISP. AL 100% | [13 empty] | AÑO 3 CON DISP. AL 100% | [13 empty] | AÑO 3 CON DISP. AL 100% | [13 empty] | AÑO 3 CON DISP. AL 100%
| 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24 |  |  | Bus Records
|  |  | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) | PU Volt | Volt (kV) |  | PU Volt | Volt (kV)
Empalme. |  |  | 0.99702 | 14.955 | 0.99736 | 14.96 | 0.99759 | 14.964 | 0.99771 | 14.966 | 0.99786 | 14.968 | 0.99798 | 14.97 | 0.99808 | 14.971 | 0.99788 | 14.968 | 0.99762 | 14.964 | 0.99726 | 14.959 | 0.997 | 14.955 |  |  | 0.99595 | 14.939 | 0.99502 | 14.925 | 0.99459 | 14.919 | 0.99499 | 14.925 | 0.99518 | 14.928 | 0.99551 | 14.933 | 0.99594 | 14.939 |  |  | 0.99625 | 14.944 | 0.99584 | 14.938 | 0.99616 | 14.942
CRAL.ACABOSE_1 |  |  | 0.9901 | 14.852 | 0.99126 | 14.869 | 0.99203 | 14.88 | 0.99243 | 14.886 | 0.99289 | 14.893 | 0.99314 | 14.897 | 0.99306 | 14.896 | 0.99222 | 14.883 | 0.9912 | 14.868 | 0.9902 | 14.853 | 0.98892 | 14.834 |  |  | 0.98705 | 14.806 | 0.98404 | 14.761 | 0.9824 | 14.736 | 0.98407 | 14.761 | 0.98467 | 14.77 | 0.98553 | 14.783 | 0.98752 | 14.813 |  |  | 0.98871 | 14.831 | 0.98753 | 14.813 | 0.98854 | 14.828
CRAL.ACABOSE_2 |  |  | 0.98977 | 14.847 | 0.99098 | 14.865 | 0.99177 | 14.876 | 0.99218 | 14.883 | 0.99265 | 14.89 | 0.99292 | 14.894 | 0.99283 | 14.892 | 0.99196 | 14.879 | 0.9909 | 14.863 | 0.98986 | 14.848 | 0.98853 | 14.828 |  |  | 0.98661 | 14.799 | 0.98351 | 14.753 | 0.98181 | 14.727 | 0.98354 | 14.753 | 0.98415 | 14.762 | 0.98504 | 14.776 | 0.98711 | 14.807 |  |  | 0.98833 | 14.825 | 0.98712 | 14.807 | 0.98816 | 14.822
E.SIRIO_4 |  |  | 0.98941 | 14.841 | 0.99066 | 14.86 | 0.99148 | 14.872 | 0.99191 | 14.879 | 0.9924 | 14.886 | 0.99267 | 14.89 | 0.99257 | 14.889 | 0.99166 | 14.875 | 0.99056 | 14.858 | 0.98949 | 14.842 | 0.9881 | 14.822 |  |  | 0.98609 | 14.791 | 0.98287 | 14.743 | 0.9811 | 14.716 | 0.9829 | 14.744 | 0.98354 | 14.753 | 0.98446 | 14.767 | 0.98661 | 14.799 |  |  | 0.98788 | 14.818 | 0.98663 | 14.799 | 0.98771 | 14.816
E.SIRIO_1 |  |  | 0.98195 | 14.729 | 0.98347 | 14.752 | 0.98445 | 14.767 | 0.98498 | 14.775 | 0.98572 | 14.786 | 0.98651 | 14.798 | 0.98751 | 14.813 | 0.98683 | 14.802 | 0.98592 | 14.789 | 0.98402 | 14.76 | 0.98347 | 14.752 |  |  | 0.98553 | 14.783 | 0.98125 | 14.719 | 0.97972 | 14.696 | 0.98101 | 14.715 | 0.98182 | 14.727 | 0.98646 | 14.797 | 0.98537 | 14.781 |  |  | 0.98652 | 14.798 | 0.9839 | 14.758 | 0.98536 | 14.78
E.SIRIO_2 |  |  | 0.98137 | 14.721 | 0.98294 | 14.744 | 0.98394 | 14.759 | 0.98449 | 14.767 | 0.98526 | 14.779 | 0.98607 | 14.791 | 0.98711 | 14.807 | 0.98641 | 14.796 | 0.98547 | 14.782 | 0.98351 | 14.753 | 0.98295 | 14.744 |  |  | 0.98512 | 14.777 | 0.98071 | 14.711 | 0.97914 | 14.687 | 0.98047 | 14.707 | 0.9813 | 14.72 | 0.98611 | 14.792 | 0.98495 | 14.774 |  |  | 0.98614 | 14.792 | 0.98343 | 14.751 | 0.98493 | 14.774
E.SIRIO_3 |  |  | 0.98012 | 14.702 | 0.98177 | 14.727 | 0.98284 | 14.743 | 0.98342 | 14.751 | 0.98423 | 14.763 | 0.9851 | 14.776 | 0.9862 | 14.793 | 0.98546 | 14.782 | 0.98448 | 14.767 | 0.9824 | 14.736 | 0.98181 | 14.727 |  |  | 0.9844 | 14.766 | 0.97973 | 14.696 | 0.97807 | 14.671 | 0.97947 | 14.692 | 0.98035 | 14.705 | 0.98564 | 14.785 | 0.98423 | 14.763 |  |  | 0.98548 | 14.782 | 0.98259 | 14.739 | 0.98418 | 14.763
I.E.S.J.VERNE |  |  | 0.97913 | 14.687 | 0.98085 | 14.713 | 0.98196 | 14.729 | 0.98256 | 14.738 | 0.9834 | 14.751 | 0.9843 | 14.765 | 0.98546 | 14.782 | 0.98469 | 14.77 | 0.98367 | 14.755 | 0.98152 | 14.723 | 0.98091 | 14.714 |  |  | 0.98401 | 14.76 | 0.97916 | 14.687 | 0.97744 | 14.662 | 0.97888 | 14.683 | 0.9798 | 14.697 | 0.98521 | 14.778 | 0.98385 | 14.758 |  |  | 0.98514 | 14.777 | 0.98211 | 14.732 | 0.98376 | 14.756
E.ALTAIR |  |  | 0.9782 | 14.673 | 0.97998 | 14.7 | 0.98114 | 14.717 | 0.98176 | 14.726 | 0.98263 | 14.739 | 0.98357 | 14.754 | 0.98477 | 14.772 | 0.98398 | 14.76 | 0.98292 | 14.744 | 0.98069 | 14.71 | 0.98006 | 14.701 |  |  | 0.98352 | 14.753 | 0.97849 | 14.677 | 0.9767 | 14.651 | 0.9782 | 14.673 | 0.97915 | 14.687 | 0.98467 | 14.77 | 0.98336 | 14.75 |  |  | 0.9847 | 14.771 | 0.98154 | 14.723 | 0.98325 | 14.749
AGRICULTORES |  |  | 0.97813 | 14.672 | 0.97992 | 14.699 | 0.98107 | 14.716 | 0.9817 | 14.725 | 0.98257 | 14.739 | 0.98352 | 14.753 | 0.98472 | 14.771 | 0.98393 | 14.759 | 0.98287 | 14.743 | 0.98062 | 14.709 | 0.98 | 14.7 |  |  | 0.9835 | 14.753 | 0.97846 | 14.677 | 0.97667 | 14.65 | 0.97817 | 14.673 | 0.97912 | 14.687 | 0.98465 | 14.77 | 0.98334 | 14.75 |  |  | 0.98469 | 14.77 | 0.98152 | 14.723 | 0.98324 | 14.749
Nudo Slack. |  |  | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 |  |  | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 | 1 | 220 |  |  | 1 | 220 | 1 | 220 | 1 | 220
AGRICULTORES_2 |  |  | 0.97811 | 14.672 | 0.9799 | 14.698 | 0.98105 | 14.716 | 0.98167 | 14.725 | 0.98255 | 14.738 | 0.98349 | 14.752 | 0.98469 | 14.77 | 0.9839 | 14.759 | 0.98284 | 14.743 | 0.9806 | 14.709 | 0.97997 | 14.7 |  |  | 0.98353 | 14.753 | 0.97848 | 14.677 | 0.9767 | 14.65 | 0.97819 | 14.673 | 0.97915 | 14.687 | 0.98467 | 14.77 | 0.98337 | 14.751 |  |  | 0.98472 | 14.771 | 0.98154 | 14.723 | 0.98326 | 14.749
E.SIRIO |  |  | 0.97805 | 14.671 | 0.97984 | 14.698 | 0.98099 | 14.715 | 0.98162 | 14.724 | 0.98249 | 14.737 | 0.98343 | 14.752 | 0.98464 | 14.77 | 0.98385 | 14.758 | 0.98279 | 14.742 | 0.98054 | 14.708 | 0.97992 | 14.699 |  |  | 0.98358 | 14.754 | 0.97853 | 14.678 | 0.97675 | 14.651 | 0.97824 | 14.674 | 0.9792 | 14.688 | 0.98473 | 14.771 | 0.98343 | 14.751 |  |  | 0.98477 | 14.772 | 0.98159 | 14.724 | 0.98331 | 14.75

## CONGESTION
AÑO 1 SIN DISP
| HORA | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| Transformador (año 1) | 60 | 49.6 | 43.2 | 39.5 | 37.3 | 34.7 | 32.6 | 30.9 | 34.1 | 38.9 | 45.1 | 49.5 | 56.6 | 71.5 | 87.6 | 94.9 | 88 | 84.8 | 80.2 | 71.8 | 71.8 | 66.4 | 73.3 | 67.9
| EMPAL-CRAL.ACABOSE_1 | 42 | 33.9 | 29.1 | 26 | 24.4 | 22.6 | 21.9 | 22.9 | 26.6 | 31 | 34.7 | 40.6 | 45.7 | 57.2 | 69.2 | 76.2 | 68.9 | 66.3 | 64.2 | 55.1 | 55.1 | 50.1 | 53.8 | 49.8
| CRAL ACABOSE_1-CRAL.ACABOSE_2 | 33 | 26.7 | 23 | 20.5 | 19.2 | 17.8 | 17.3 | 18.1 | 20.9 | 24.4 | 27.3 | 31.9 | 35.9 | 44.8 | 54.1 | 59.6 | 53.9 | 51.9 | 50.3 | 43.2 | 43.2 | 39.3 | 42.2 | 39.1
| CRAL ACABOSE_2-E.SIRIO_4 | 24 | 19.5 | 16.8 | 15 | 14.1 | 13.1 | 12.7 | 13.2 | 15.4 | 17.9 | 20 | 23.4 | 26.3 | 32.9 | 39.7 | 43.7 | 39.5 | 38.1 | 36.8 | 31.7 | 31.7 | 28.8 | 30.9 | 28.6
| E.SIRIO_1 | 53 | 45.6 | 40.2 | 37.2 | 35.5 | 33.1 | 30.4 | 26.7 | 28.1 | 31.3 | 37.5 | 38.7 | 44.9 | 57.3 | 70.9 | 75.5 | 71.8 | 69.3 | 64.1 | 59.8 | 59.8 | 56.3 | 63.6 | 58.9
| E.SIRIO_2 | 48 | 40.1 | 35.9 | 33.3 | 31.7 | 29.6 | 27.2 | 24 | 25.7 | 28 | 33.6 | 34.6 | 40.2 | 51.1 | 63 | 66.9 | 63.8 | 61.5 | 57 | 53.3 | 53.3 | 50.2 | 56.5 | 52.5
| E.SIRIO_3 | 31 | 25.9 | 23.2 | 21.5 | 20.5 | 19.1 | 17.6 | 15.5 | 16.6 | 18.1 | 21.7 | 22.3 | 25.9 | 32.9 | 40.6 | 43.2 | 41.1 | 39.7 | 36.7 | 34.4 | 34.4 | 32.4 | 36.5 | 33.8
| I.E.S.J.VERNE | 18 | 15 | 13.4 | 12.5 | 11.9 | 11.1 | 10.2 | 9 | 9.6 | 10.5 | 12.6 | 12.9 | 15 | 19.1 | 23.5 | 25 | 23.8 | 23 | 21.3 | 19.9 | 19.9 | 18.8 | 21.1 | 19.6
| ESTRELLA.ALTAIR | 16 | 13.7 | 12.2 | 11.4 | 10.8 | 10.1 | 9.3 | 8.2 | 8.8 | 9.6 | 11.4 | 11.8 | 13.7 | 17.4 | 21.4 | 22.8 | 21.7 | 21 | 19.4 | 18.1 | 18.1 | 17.1 | 19.2 | 17.9
| AGRICULTORES | 8 | 6.7 | 6 | 5.6 | 5.3 | 5 | 4.6 | 4 | 4.3 | 4.7 | 5.6 | 5.8 | 6.7 | 8.5 | 10.5 | 11.2 | 10.7 | 10.3 | 9.5 | 8.9 | 8.9 | 8.4 | 9.4 | 8.8
| AGRICULTORES_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E.SIRIO | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| AÑO 2 SIN DISP | [27 empty] | Crecimiento
| HORA | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 |  |  |  | 1% | 2% | 3% | 4% | 5%
| Transformador (año 2) | 62.7 | 51.7 | 45.9 | 41.9 | 39.2 | 36.5 | 33.3 | 32.5 | 36.2 | 40.8 | 47.2 | 52 | 59.5 | 75.2 | 92.1 | 99.7 | 92.5 | 89.1 | 84.3 | 75.2 | 65.6 | 69.9 | 77.1 | 71.3 |  |  | Congestión % | 89.2 | 89.2 | 89.2 | 89.2 | 89.2 | 3 | Año
| EMPAL-CRAL.ACABOSE_1 | 44.3 | 35.6 | 31.4 | 28.1 | 25.6 | 23.8 | 23 | 24.1 | 27.9 | 32.6 | 36.3 | 42.6 | 48 | 60.1 | 72.7 | 80.1 | 72.4 | 69.7 | 67.5 | 57.7 | 51.3 | 52.6 | 56.5 | 52.3 |  |  |  | 90.2 | 91.2 | 92.2 | 93.2 | 94.3 | 4
| CRAL ACABOSE_1-CRAL.ACABOSE_2 | 34.8 | 28 | 24.9 | 22.3 | 20.2 | 18.8 | 18.1 | 19 | 22 | 25.6 | 28.5 | 33.4 | 37.7 | 47.1 | 56.8 | 62.6 | 56.6 | 54.5 | 52.8 | 45.2 | 40.2 | 41.3 | 44.3 | 41 |  |  |  | 91.2 | 93.2 | 95.2 | 97.2 | 99.3 | 5
| CRAL ACABOSE_2-E.SIRIO_4 | 25.5 | 20.5 | 18.5 | 16.6 | 14.8 | 13.7 | 13.3 | 13.9 | 16.1 | 18.8 | 21 | 24.6 | 27.6 | 34.5 | 41.7 | 45.8 | 41.5 | 40 | 38.7 | 33.3 | 29.5 | 30.2 | 32.5 | 30.1 |  |  |  | 92.2 | 95.2 | 98.2 | 101.2 | 104.3 | 6
| E.SIRIO_1 | 56.1 | 47.2 | 42.2 | 39.1 | 37.2 | 34.7 | 30.4 | 28.1 | 30.1 | 32.9 | 39.4 | 40.7 | 47.2 | 60.2 | 74.5 | 79.3 | 75.5 | 72.8 | 67.3 | 62.7 | 53.8 | 59.2 | 66.8 | 61.9 |  |  |  | 93.2 | 97.2 | 101.2 | 105.2 | 109.3 | 7
| E.SIRIO_2 | 50 | 42.1 | 37.7 | 35 | 33.3 | 31.1 | 27.2 | 25.2 | 27 | 29.5 | 35.2 | 36.3 | 42.2 | 53.6 | 66.1 | 70.3 | 66.9 | 64.6 | 59.8 | 55.9 | 47.9 | 52.7 | 59.3 | 55.1
| E.SIRIO_3 | 32.2 | 27.2 | 24.3 | 22.5 | 21.5 | 20.1 | 17.6 | 16.2 | 17.4 | 19 | 22.7 | 23.4 | 27.2 | 34.6 | 42.6 | 45.3 | 43.2 | 41.7 | 38.6 | 36.1 | 30.9 | 34 | 38.3 | 35.5
| I.E.S.J.VERNE | 18.7 | 15.8 | 14.1 | 13.1 | 12.5 | 11.6 | 10.2 | 9.4 | 10.1 | 11 | 13.2 | 13.6 | 15.8 | 20 | 24.7 | 26.3 | 25 | 24.2 | 22.4 | 20.9 | 17.9 | 19.7 | 22.2 | 20.6
| ESTRELLA.ALTAIR | 17 | 14.4 | 12.9 | 11.9 | 11.4 | 10.6 | 9.3 | 8.6 | 9.2 | 10 | 12 | 12.4 | 14.4 | 18.2 | 22.5 | 23.9 | 22.8 | 22 | 20.4 | 19 | 16.3 | 18 | 20.2 | 18.8
| AGRICULTORES | 8.4 | 7.1 | 6.3 | 5.8 | 5.6 | 5.2 | 4.6 | 4.2 | 4.5 | 4.9 | 5.9 | 6.1 | 7.1 | 9 | 11.1 | 11.7 | 11.2 | 10.8 | 10 | 9.4 | 8 | 8.8 | 9.9 | 9.2
| AGRICULTORES_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E.SIRIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
=
|  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
AÑO 3 SIN DISP
| HORA | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| Transformador (año 3) | 65.9 | 54.3 | 47.7 | 43.5 | 41.2 | 38.3 | 36 | 34.1 | 38 | 42.5 | 49.7 | 54.9 | 62.8 | 79 | 96.8 | 104.8 | 97.2 | 92.8 | 88.5 | 79.3 | 69 | 73.4 | 81 | 75
| EMPAL-CRAL.ACABOSE_1 | 46.6 | 37.4 | 32.2 | 28.7 | 26.9 | 25 | 24.1 | 25.3 | 29.3 | 33.5 | 38.3 | 45.3 | 50.4 | 63.1 | 76.4 | 84.1 | 76 | 71.9 | 70.9 | 60.8 | 53.9 | 55.2 | 59.4 | 54.9
| CRAL ACABOSE_1-CRAL.ACABOSE_2 | 36.6 | 29.4 | 25.3 | 22.6 | 21.2 | 19.7 | 19 | 19.9 | 23.1 | 26.9 | 30.1 | 35.6 | 39.6 | 49.4 | 59.7 | 65.7 | 59.4 | 56 | 55.4 | 47.7 | 42.3 | 43.3 | 46.6 | 43.1
| CRAL ACABOSE_2-E.SIRIO_4 | 26.8 | 21.5 | 18.5 | 16.6 | 15.6 | 14.4 | 13.9 | 14.6 | 16.9 | 19.7 | 22.1 | 26.1 | 29 | 36.2 | 43.7 | 48.1 | 43.6 | 40.7 | 40.6 | 34.9 | 31 | 31.8 | 34.1 | 31.6
| E.SIRIO_1 | 58.9 | 49.6 | 44.3 | 41 | 39.1 | 36.5 | 33.6 | 29.5 | 31.6 | 34.5 | 41.4 | 43.4 | 50.1 | 63.3 | 78.3 | 83.3 | 79.3 | 76.5 | 70.7 | 66 | 56.5 | 62.2 | 70.2 | 65
| E.SIRIO_2 | 52.5 | 44.2 | 39.6 | 36.6 | 35 | 32.6 | 30.1 | 26.4 | 28.3 | 30.9 | 37 | 38.8 | 44.7 | 56.3 | 69.4 | 73.8 | 70.3 | 67.8 | 62.8 | 58.7 | 50.3 | 55.4 | 62.3 | 57.8
| E.SIRIO_3 | 33.8 | 28.5 | 25.5 | 23.6 | 22.6 | 21 | 19.4 | 17 | 18.3 | 19.9 | 23.9 | 25.1 | 29 | 36.3 | 44.8 | 47.6 | 45.3 | 43.7 | 40.5 | 37.9 | 32.5 | 35.7 | 40.2 | 37.3
| I.E.S.J.VERNE | 19.6 | 16.6 | 14.8 | 13.6 | 13.1 | 12.2 | 11.3 | 9.9 | 10.6 | 11.6 | 13.8 | 14.6 | 17 | 21.1 | 26 | 27.6 | 26.3 | 25.4 | 23.5 | 21.9 | 18.8 | 20.7 | 23.3 | 21.6
| ESTRELLA.ALTAIR | 17.9 | 15.1 | 13.5 | 12.4 | 11.9 | 11.1 | 10.2 | 9 | 9.6 | 10.5 | 12.6 | 13.2 | 15.6 | 19.2 | 23.6 | 25.1 | 23.9 | 23.1 | 21.4 | 20 | 17.1 | 18.9 | 21.2 | 19.7
| AGRICULTORES | 8.8 | 7.4 | 6.6 | 6 | 5.9 | 5.5 | 5 | 4.4 | 4.7 | 5.2 | 6.2 | 6.5 | 7.4 | 9.4 | 11.6 | 12.3 | 11.7 | 11.3 | 10.5 | 9.8 | 8.4 | 9.3 | 10.4 | 9.7
| AGRICULTORES_2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E.SIRIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grado de congestión en % para las 16:00 |  | 1: AÑO 0; 2: AÑO 1; 3: AÑO 2; 4: AÑO 3; 16: 15.6
Transformador |  | 1: 0.23; 2: 94.9; 3: 99.7; 4: 104.8
"Empalme-Corral del Acabose" | EMPAL-CRAL.ACABOSE_1 | 1: 0.73; 2: 76.2; 3: 80.1; 4: 84.1
| CRAL ACABOSE_1-CRAL.ACABOSE_2 | 1: 0.57; 2: 59.6; 3: 62.6; 4: 65.7
| CRAL ACABOSE_2-E.SIRIO_4 | 1: 0.41; 2: 43.7; 3: 45.8; 4: 48.1
"Empalme-Estrella Sirio" | E.SIRIO_1 | 1: 0.72; 2: 75.5; 3: 79.3; 4: 83.3
| E.SIRIO_2 | 1: 0.64; 2: 66.9; 3: 70.3; 4: 73.8
| E.SIRIO_3 | 1: 0.41; 2: 43.2; 3: 45.3; 4: 47.6
| I.E.S.J.VERNE | 1: 0.24; 2: 25; 3: 26.3; 4: 27.6
| ESTRELLA.ALTAIR | 1: 0.22; 2: 22.8; 3: 23.9; 4: 25.1
| AGRICULTORES | 1: 0.11; 2: 11.2; 3: 11.7; 4: 12.3
| AGRICULTORES_2 | 1: 0; 2: 0; 3: 0; 4: 0
| E.SIRIO | 1: 0; 2: 0; 3: 0; 4: 0
distribución de congestion del trafo.
| 30-40% | 2: 7; 3: 5; 4: 4
| 40-50% | 2: 4; 3: 4; 4: 5
| 50-60% | 2: 1; 3: 3; 4: 2
| 60-70% | 2: 3; 3: 3; 4: 3
| 70-80% | 2: 4; 3: 4; 4: 4
| 80-100% | 2: 5; 3: 5; 4: 6
AÑO 3 CON DISP AL 25%
| HORA | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| Congestión Transformador | 65.9 | 58.8 | 52.2 | 48 | 45.7 | 42.8 | 40.4 | 38.6 | 42.5 | 47.4 | 54.2 | 59.2 | 62.8 | 75 | 92.8 | 100.8 | 93.2 | 89.8 | 76.7 | 75.4 | 69 | 69.5 | 77 | 71
| EMPAL-CRAL.ACABOSE_1 | 46.6 | 39.3 | 34.1 | 30.7 | 28.9 | 26.9 | 26.1 | 27.2 | 31.3 | 36.2 | 40.3 | 46.8 | 50.4 | 61.4 | 74.6 | 82.4 | 74.3 | 71.7 | 69 | 59.1 | 53.9 | 53.5 | 57.7 | 53.2
| CRAL ACABOSE_1-CRAL.ACABOSE_2 | 36.6 | 30.7 | 26.6 | 23.9 | 22.5 | 21 | 20.3 | 21.2 | 24.4 | 28.2 | 31.4 | 36.5 | 39.6 | 48.3 | 58.6 | 64.6 | 58.3 | 56.3 | 54.2 | 46.5 | 42.3 | 42.2 | 45.4 | 41.9
| CRAL ACABOSE_2-E.SIRIO_4 | 26.8 | 22.2 | 19.2 | 17.3 | 16.2 | 15.1 | 14.6 | 15.3 | 17.6 | 20.4 | 22.8 | 26.5 | 29 | 35.6 | 43.1 | 47.5 | 43 | 41.6 | 40 | 34.3 | 31 | 31.2 | 33.5 | 31
| E.SIRIO_1 | 58.9 | 54.8 | 49.6 | 46.2 | 44.4 | 41.7 | 38.7 | 34.7 | 36.8 | 39.8 | 46.6 | 48 | 50.1 | 58.7 | 73.8 | 78.7 | 74.7 | 71.9 | 54 | 61.5 | 56.5 | 57.7 | 65.6 | 60.5
| E.SIRIO_2 | 52.5 | 48.7 | 44.1 | 41.1 | 39.5 | 37.1 | 34.5 | 30.9 | 32.8 | 35.4 | 41.5 | 42.7 | 44.7 | 52.4 | 65.6 | 69.9 | 66.4 | 64 | 47.1 | 54.8 | 50.3 | 51.5 | 58.4 | 53.9
| E.SIRIO_3 | 33.8 | 32.4 | 29.4 | 27.4 | 26.4 | 24.9 | 23.2 | 20.9 | 22.2 | 23.8 | 27.7 | 28.5 | 29 | 33 | 41.5 | 44.3 | 42 | 40.4 | 26 | 34.5 | 32.5 | 32.4 | 36.9 | 34
| I.E.S.J.VERNE | 19.6 | 19.8 | 18.1 | 16.9 | 16.3 | 15.5 | 14.4 | 13.2 | 13.9 | 14.8 | 17.1 | 17.5 | 17 | 18.3 | 23.2 | 24.8 | 23.5 | 22.6 | 20.8 | 19.2 | 18.8 | 18 | 20.6 | 18.9
| ESTRELLA.ALTAIR | 17.9 | 17.6 | 16.1 | 15 | 14.5 | 13.7 | 12.8 | 11.6 | 12.3 | 13.1 | 15.2 | 15.6 | 15.6 | 17 | 21.4 | 22.9 | 21.7 | 20.9 | 19.2 | 17.8 | 17.1 | 16.7 | 19 | 17.5
| AGRICULTORES | 8.8 | 9.4 | 8.6 | 8 | 7.8 | 7.4 | 6.9 | 6.4 | 6.7 | 7.1 | 8.1 | 8.3 | 7.4 | 7.8 | 10 | 10.7 | 10.1 | 9.7 | 8.9 | 8.2 | 8.4 | 7.6 | 8.8 | 8
| AGRICULTORES_2 | 0 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 0 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 0 | 1.3 | 1.3 | 1.3
| E.SIRIO | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0.7 | 0.7 | 0.7
AÑO 3 CON DISP AL 50%
| HORA | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| TRAFO |  | 63.4 | 56.8 | 52.5 | 50.3 | 47.4 | 45 | 43.2 | 47.1 | 52 | 58.8 | 63.7 |  | 71.1 | 88.8 | 96.8 | 89.2 | 85.8 | 72.9 | 71.4 |  | 65.5 | 73.1 | 67.1
| EMPAL-CRAL.ACABOSE_1 |  | 41.3 | 36.1 | 32.7 | 30.9 | 28.9 | 28.1 | 29.2 | 33.3 | 38.2 | 42.3 | 48.8 |  | 59.6 | 72.8 | 80.6 | 72.5 | 69.9 | 67.3 | 57.3 |  | 51.8 | 55.9 | 51.4
| CRAL ACABOSE_1-CRAL.ACABOSE_2 |  | 32 | 27.9 | 25.2 | 23.8 | 22.3 | 21.6 | 22.5 | 25.7 | 29.5 | 32.7 | 37.8 |  | 47.1 | 57.4 | 63.4 | 57.1 | 55.2 | 53.1 | 45.4 |  | 41 | 44.2 | 40.8
| CRAL ACABOSE_2-E.SIRIO_4 |  | 22.9 | 19.9 | 17.9 | 16.9 | 15.8 | 15.3 | 15.9 | 18.3 | 21.1 | 23.4 | 27.2 |  | 35 | 42.5 | 46.9 | 42.4 | 41 | 39.4 | 33.7 |  | 30.6 | 32.9 | 30.4
| E.SIRIO_1 |  | 60.2 | 54.9 | 51.6 | 49.7 | 47.1 | 44.1 | 40.1 | 42.3 | 45.2 | 52 | 53.3 |  | 54.2 | 69.2 | 74.1 | 70.1 | 67.3 | 49.9 | 56.9 |  | 53.1 | 61 | 55.9
| E.SIRIO_2 |  | 53.3 | 48.7 | 45.7 | 44.1 | 41.8 | 39.1 | 35.6 | 37.5 | 40.1 | 46.1 | 47.3 |  | 48.5 | 61.7 | 66 | 62.5 | 60.1 | 43.7 | 50.9 |  | 47.6 | 54.5 | 50
| E.SIRIO_3 |  | 36.4 | 33.4 | 31.4 | 30.4 | 28.9 | 27.2 | 25 | 26.2 | 27.9 | 31.7 | 32.5 |  | 29.7 | 38.1 | 40.9 | 38.7 | 37.1 | 23.5 | 31.3 |  | 29.1 | 33.6 | 30.7
| I.E.S.J.VERNE |  | 23.1 | 21.4 | 20.2 | 19.7 | 18.8 | 17.8 | 16.6 | 17.3 | 18.2 | 20.4 | 20.9 |  | 15.7 | 20.5 | 22.1 | 20.8 | 19.9 | 18.1 | 16.6 |  | 15.3 | 17.9 | 16.2
| ESTRELLA.ALTAIR |  | 20.3 | 18.7 | 17.7 | 17.2 | 16.4 | 15.5 | 14.3 | 15 | 15.8 | 17.9 | 18.3 |  | 14.8 | 19.3 | 20.7 | 19.5 | 18.7 | 17.1 | 15.6 |  | 14.5 | 16.9 | 15.4
| AGRICULTORES |  | 11.4 | 10.6 | 10 | 9.9 | 9.5 | 9 | 8.5 | 8.8 | 9.2 | 10.2 | 10.4 |  | 6.3 | 8.4 | 9.1 | 8.6 | 8.2 | 7.3 | 6.7 |  | 6.1 | 7.3 | 6.5
| AGRICULTORES_2 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 |  | 2.7 | 2.7 | 2.7
| E.SIRIO |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 |  | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 |  | 1.3 | 1.3 | 1.3
AÑO 3 CON DISP AL 75%
| HORA | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| TRAFO |  | 58.8 | 61.4 | 57.1 | 54.9 | 52 | 49.6 | 47.8 | 51.7 | 56.5 | 63.4 | 68.3 |  | 67.3 | 85 | 93 | 85.4 | 82 | 69.2 | 67.6 |  | 61.8 | 69.3 | 63.3 | 3.8 | 3.8
| EMPAL-CRAL.ACABOSE_1 |  | 39.3 | 38.1 | 34.6 | 32.9 | 30.9 | 30.1 | 31.2 | 35.2 | 40.1 | 44.2 | 50.7 |  | 57.9 | 71.1 | 78.9 | 70.8 | 68.2 | 65.6 | 55.6 |  | 50.1 | 54.2 | 49.7 | 1.7 | 1.7
| CRAL ACABOSE_1-CRAL.ACABOSE_2 |  | 30.7 | 29.2 | 26.5 | 25.1 | 23.6 | 22.9 | 23.8 | 27 | 30.8 | 34 | 39.1 |  | 46 | 56.3 | 62.3 | 56 | 54 | 52 | 44.2 |  | 39.9 | 43.1 | 39.7 | 1.1 | 1.1
| CRAL ACABOSE_2-E.SIRIO_4 |  | 22.2 | 20.6 | 18.6 | 17.6 | 16.5 | 16 | 16.6 | 19 | 21.7 | 24.1 | 27.8 |  | 34.4 | 41.9 | 46.3 | 41.8 | 40.4 | 38.8 | 33.1 |  | 30 | 32.3 | 29.8 | 0.6 | 0.6
| E.SIRIO_1 |  | 54.8 | 60.3 | 56.9 | 55.1 | 52.5 | 49.5 | 45.5 | 47.7 | 50.6 | 57.4 | 58.7 |  | 49.9 | 64.8 | 69.7 | 65.8 | 63 | 46.2 | 52.6 |  | 48.9 | 56.7 | 51.6 | 4.3 | 4.3
| E.SIRIO_2 |  | 48.7 | 53.3 | 50.3 | 48.7 | 46.4 | 43.8 | 40.3 | 42.1 | 44.7 | 50.7 | 51.9 |  | 44.9 | 57.9 | 62.3 | 58.8 | 56.4 | 40.5 | 47.3 |  | 44 | 50.9 | 46.4 | 3.6 | 3.6 |  | 20.6
| E.SIRIO_3 |  | 32.4 | 37.3 | 35.4 | 34.4 | 32.9 | 31.2 | 29 | 30.2 | 31.9 | 35.7 | 36.4 |  | 26.7 | 35 | 37.8 | 35.6 | 34 | 21.6 | 28.2 |  | 26.1 | 30.5 | 27.7 | 3 | 3.1 |  | 76.2
| I.E.S.J.VERNE |  | 19.8 | 24.7 | 23.6 | 23.1 | 22.2 | 21.2 | 20 | 20.7 | 21.6 | 23.8 | 24.2 |  | 13.4 | 18.1 | 19.7 | 18.4 | 17.5 | 15.7 | 14.2 |  | 13.1 | 15.5 | 13.9 | 2.3 | 2.4
| ESTRELLA.ALTAIR |  | 17.6 | 21.4 | 20.3 | 19.9 | 19.1 | 18.1 | 17 | 17.6 | 18.5 | 20.5 | 20.9 |  | 12.9 | 17.3 | 18.7 | 17.5 | 16.7 | 15.1 | 13.7 |  | 12.6 | 14.9 | 13.4 | 2 | 2
| AGRICULTORES |  | 9.4 | 12.6 | 12.1 | 11.9 | 11.5 | 11 | 10.5 | 10.8 | 11.2 | 12.2 | 12.4 |  | 5.1 | 7.1 | 7.8 | 7.2 | 6.8 | 6.1 | 5.5 |  | 5 | 6 | 5.4 | 1.1 | 1.3
| AGRICULTORES_2 |  | 1.5 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 4 | 4 | -1.3 | -1.3
| E.SIRIO |  | 0.7 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | -0.7 | -0.7
AÑO 3 CON DISP AL 100%
| HORA | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| TRAFO | 65.9 | 72.7 | 66.1 | 61.9 | 59.6 | 56.8 | 54.4 | 52.6 | 56.4 | 61.3 | 68.1 | 73 | 62.8 | 63.6 | 81.2 | 89.2 | 81.6 | 78.2 | 64 | 62.1 | 69 | 56.3 | 65.6 | 59.6 | 3.7 | 3.7
| EMPAL-CRAL.ACABOSE_1 | 46.6 | 45.3 | 40.1 | 36.7 | 34.9 | 33 | 32.1 | 33.3 | 37.3 | 42.2 | 46.3 | 52.8 | 50.4 | 56.2 | 69.4 | 77.2 | 69.1 | 66.5 | 63 | 53.1 | 53.9 | 47.6 | 52.5 | 48.1 | 1.6 | 1.7
| CRAL ACABOSE_1-CRAL.ACABOSE_2 | 36.6 | 34.6 | 30.6 | 27.9 | 26.5 | 25 | 24.3 | 25.2 | 28.4 | 32.1 | 35.4 | 40.4 | 39.6 | 44.9 | 55.1 | 61.1 | 54.9 | 52.9 | 50.3 | 42.6 | 42.3 | 38.3 | 42 | 38.6 | 1.1 | 1.1
| CRAL ACABOSE_2-E.SIRIO_4 | 26.8 | 24.3 | 21.3 | 19.3 | 18.3 | 17.2 | 16.7 | 17.3 | 19.6 | 22.4 | 24.8 | 28.5 | 29 | 33.9 | 41.4 | 45.7 | 41.2 | 39.8 | 37.9 | 32.3 | 31 | 29.1 | 31.7 | 29.2 | 0.6 | 0.6
| E.SIRIO_1 | 58.9 | 71.1 | 65.9 | 62.5 | 60.7 | 58.1 | 55.1 | 51.2 | 53.3 | 56.1 | 62.9 | 64.3 | 50.1 | 45.8 | 60.6 | 65.5 | 61.5 | 58.8 | 41.2 | 46.6 | 56.5 | 42.9 | 52.6 | 47.6 | 4 | 4.1
| E.SIRIO_2 | 52.5 | 62.6 | 58 | 55 | 53.5 | 51.2 | 48.6 | 45.1 | 46.9 | 49.5 | 55.4 | 56.6 | 44.7 | 41.4 | 54.3 | 58.6 | 55.2 | 52.8 | 36.4 | 42.1 | 50.3 | 38.8 | 47.3 | 42.9 | 3.5 | 3.6
| E.SIRIO_3 | 33.8 | 44.4 | 41.5 | 39.5 | 38.5 | 37.1 | 35.4 | 33.2 | 34.4 | 36 | 39.8 | 40.6 | 29 | 23.9 | 32.1 | 34.8 | 32.6 | 31.1 | 19.7 | 24.1 | 32.5 | 22.1 | 27.6 | 24.9 | 2.8 | 2.9
| I.E.S.J.VERNE | 19.6 | 29.9 | 28.2 | 27.1 | 26.5 | 25.7 | 24.7 | 23.5 | 24.2 | 25.1 | 27.3 | 27.7 | 17 | 11.5 | 15.9 | 17.4 | 16.2 | 15.4 | 12.8 | 11.5 | 18.8 | 10.6 | 13.5 | 12 | 1.9 | 2
| ESTRELLA.ALTAIR | 17.9 | 25.7 | 24.1 | 23.1 | 22.6 | 21.9 | 20.9 | 19.8 | 20.4 | 21.3 | 23.3 | 23.7 | 15.6 | 11.3 | 15.4 | 16.8 | 15.7 | 14.9 | 12.5 | 11.3 | 17.1 | 10.3 | 13.1 | 11.7 | 1.7 | 1.8
| AGRICULTORES | 8.8 | 15.5 | 14.7 | 14.2 | 14 | 13.6 | 13.1 | 12.6 | 12.9 | 13.3 | 14.3 | 14.5 | 7.4 | 4.5 | 6.1 | 6.7 | 6.2 | 5.9 | 5.1 | 4.7 | 8.4 | 4.5 | 5.2 | 4.7 | 0.7 | 0.8
| AGRICULTORES_2 | 0 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 0 | 5.4 | 5.3 | 5.3 | 5.3 | 5.3 | 6 | 6 | 0 | 6 | 5.3 | 5.3 | -1.3 | -1.3
| E.SIRIO | 0 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 3 | 3 | 0 | 3 | 2.7 | 2.7

## CON DISPOSITIVO
CARACTERISTICAS DEL ALMACENAMIENTO
Energía (MWh) | Capacidad | Energía/nodo(MWh) | Valle | Pico | Valle | Pico
4.9225 | 25% | 0.4475 | 0.040682 | 0.04475 | 0.04475 | 0.040275
9.845 | 50% | 0.895 | 0.081364 | 0.0895 | 0.0895 | 0.08055
14.7675 | 75% | 1.3425 | 0.12205 | 0.13425 | 0.13425 | 0.12083
19.69 | 100% | 1.79 | 0.16273 | 0.179 | 0.179 | 0.1611
|  |  | Sin contar el rendimiento |  | Contando el Rendimiento
Máximo | 19.69
Horas Valle | 11 | 0.44303 | 19.69
Horas Pico | 10 | 0.44303 | 16.11
Resto horas neutras
Se ha tomado rendimiento para este caso del 81 %.
90% en carga y 90% en decarga.

## DEMANDA CON DISP
| 25% |  |  | 50% |  |  | 75% |  |  | 100% |  |  |  | AÑO 3 sin dispositivo
Hora | P (MW) | Q(Mvar) | S (Mva) | P (MW) | Q(Mvar) | S (Mva) | P (MW) | Q(Mvar) | S (Mva) | P (MW) | Q(Mvar) | S (Mva) |  | MW | Media
1 | 5.7069 |  |  | 5.7069 |  |  | 5.7069 |  |  | 5.7069 |  |  | 5.7558 | 5.7069 | 5.5749 | 1.898
2 | 5.274 | 2.596 |  | 5.78 | 2.598 |  | 6.276 | 2.6 |  | 6.787 | 2.602 |  | 5.7558 | 4.7118 | 5.5749 | 0.77171
3 | 4.697 | 2.283 |  | 5.202 | 2.285 |  | 5.696 | 2.287 |  | 6.203 | 2.289 |  | 5.7558 | 4.1482 | 5.5749
4 | 4.321 | 2.08 |  | 4.825 | 2.082 |  | 5.319 | 2.083 |  | 5.825 | 2.085 |  | 5.7558 | 3.7872 | 5.5749
5 | 4.123 | 1.969 |  | 4.627 | 1.971 |  | 5.12 | 1.972 |  | 5.626 | 1.974 |  | 5.7558 | 3.5846 | 5.5749
6 | 3.87 | 1.832 |  | 4.373 | 1.834 |  | 4.876 |  |  | 5.379 |  |  | 5.7558 | 3.338 | 5.5749
7 | 3.657 | 1.721 |  | 4.16 | 1.723 |  | 4.866 | 1.835 |  | 5.157 | 1.726 |  | 5.7558 | 3.1354 | 5.5749
8 | 3.501 | 1.631 |  | 4.003 | 1.632 |  | 4.654 | 1.724 |  | 4.999 | 1.635 |  | 5.7558 | 2.9767 | 5.5749
9 | 3.84 | 1.818 |  | 4.343 | 1.819 |  | 4.835 | 1.821 |  | 5.34 | 1.822 |  | 5.7558 | 3.3112 | 5.5749
10 | 4.27 | 2.052 |  | 4.773 | 2.053 |  | 5.266 | 2.055 |  | 5.771 | 2.056 |  | 5.7558 | 3.7338 | 5.5749
11 | 4.873 | 2.379 |  | 5.378 | 2.381 |  | 5.872 | 2.383 |  | 6.378 | 2.385 |  | 5.7558 | 4.3239 | 5.5749
12 | 5.307 | 2.614 |  | 5.811 | 2.616 |  | 6.306 | 2.618 |  | 6.813 | 2.62 |  | 5.7558 | 4.7464 | 5.5749
13 | 5.4157 |  |  | 5.4157 |  |  | 5.4157 |  |  | 5.4157 |  |  | 5.7558 | 5.4157 | 5.5749
14 | 6.487 | 3.773 |  | 6.025 | 3.771 |  | 5.575 | 3.769 |  | 5.126 | 3.767 |  | 5.7558 | 6.8248 | 5.5749
15 | 8.049 | 4.623 |  | 7.585 | 4.621 |  | 7.132 | 4.618 |  | 6.68 | 4.615 |  | 5.7558 | 8.3307 | 5.5749
16 | 8.754 | 5.008 |  | 8.288 | 5.005 |  | 7.835 | 5.002 |  | 7.382 | 5 |  | 5.7558 | 9.0087 | 5.5749 |  | Grado | desviación Estandar
17 | 8.085 | 4.643 |  | 7.62 | 4.64 |  | 7.168 | 4.638 |  | 6.716 | 4.635 |  | 5.7558 | 8.366 | 5.5749 |  | sin disositivo | 1.9
18 | 7.791 | 4.473 |  | 7.327 | 4.47 |  | 6.842 | 4.529 |  | 6.423 | 4.465 |  | 5.7558 | 8.0666 | 5.5749 |  | 25% | 1.5074
19 | 6.4 | 4.225 |  | 5.938 | 4.223 |  | 5.448 | 4.22 |  | 4.814 | 4.217 |  | 5.7558 | 7.6349 | 5.5749 |  | 50% | 1.1287
20 | 6.515 | 3.778 |  | 6.053 | 3.785 |  | 5.603 | 3.783 |  | 5.147 |  |  | 5.7558 | 6.8514 | 5.5749 |  | 75% | 0.82053
21 | 5.9707 |  |  | 5.9707 |  |  | 5.9707 | 3.783 |  | 5.9707 |  |  | 5.7558 | 5.9707 | 5.5749 |  | 100% | 0.77
22 | 5.998 | 3.506 |  | 5.537 | 3.504 |  | 5.088 | 3.502 |  | 4.415 | 3.499 |  | 5.7558 | 6.3495 | 5.5749
23 | 6.663 | 3.869 |  | 6.2 | 3.867 |  | 5.749 | 3.864 |  | 5.292 |  |  | 5.7558 | 6.9925 | 5.5749
24 | 6.134 | 3.581 |  | 5.672 | 3.579 |  | 5.223 | 3.576 |  | 4.774 | 3.574 |  | 5.7558 | 6.4817 | 5.5749
|  |  |  | 0.503 |  |  | 0.212